## SystemNrData
systemNr | systemType | isInARoom
=310 | Sanitær | FALSE
=320.001 | Heath pumps | FALSE
=320.002 | PCM | FALSE
=320.003 | Varmestokk | FALSE
=320.004 | District heating | FALSE
=360.001 | Ventilation 1-4 fl West | FALSE
=360.002 | Ventilation 1-4 fl East | FALSE
=360.003 | Ventilation Research cell 2 | FALSE
=360.004 | Ventilation Research cell 1 | FALSE
=360.007 | Inverter room | TRUE
=370.001 | Kjøleanlegg | FALSE
=370.010 | Inverter room | FALSE
=434.101 | Technical | FALSE
=471.001 | Solar panels | FALSE
=577.001 | Electrical measures | FALSE
=569 | Roomcontrol | TRUE | Denne brukes kun til å finne etg og rom og dekker også f.eks.=569.220
=577.001 | Kraftflyt | FALSE

## =310.001
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=310.001 | =434-OU001 | 10.205.34.11 | 2443266 | RT402 | Flow temp Tappevann | "338'310'001'TDhw402'TSen", | RT402 Tappevannstemperatur | R | 1 | 1 min
|  |  |  | RT501 | Return temp Tappevann | "338'310'001'TrtDhw501'TSen", | RT501 Retur tappevannstemp | R | 1 | 1 min
|  |  |  | RT401 | Temperature tank | "338'310'001'TTnkBtm'TSen", | RT401 Tappevannstemperatur | R | 1 | 1 min
|  |  |  | RT403 | Flow temp energy 320 | "338'310'001'MtrEg'TFl", | Turtemperatur Energimåler | R | 1 | 1 min
|  |  |  | RT502 | Return temp energy 320 | "338'310'001'MtrEg'TRt", | Returtemperatur Energimåler | R | 1 | 1 min
|  |  |  | OE011 | Active effect energy | "338'310'001'MtrEg'Pwr", | Effekt | R | 2 | 1 min
|  |  |  | OE011 | Cummulated energy heating | "338'310'001'MtrEg'CumEg", | Kumulert energi varme | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'310'001'MtrEg'CumVlm", | Kumulert volum (mengde) | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'310'001'MtrEg'Fl", | StrÃ¸mning | R | 2 | 1 min
|  |  |  | OV401 | Cummulated volume m3 | "338'310'001'WMtr'CumVlm", | Kumulert volum (mengde) | R | 2 | 1 min
|  |  |  | OV401 | Flow m3/h | "338'310'001'WMtr'Fl", | StrÃ¸mning | R | 2 | 1 min
|  |  |  | OV402 | Cummulated volume m3 | "338'310'001'WMtr1'CumVlm", | Kumulert volum (mengde) | R | 2 | 1 min
|  |  |  | OV402 | Flow m3/h | "338'310'001'WMtr1'Fl", | StrÃ¸mning | R | 2 | 1 min
|  |  |  | OE00X | Energy loss circulation | "338'310'001'EffKalk", | Kalkulert tap i tappevannsledning | R | 2 | 1
Note on E8: Thomas Elvrum Lassen: Stemmer denne merkingen?

## =320.001
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=320.001 | =434-OU001 | 10.205.34.11 | 2443266 | RT401 | Flow temp energy Hpu | "338'320'001'MtrEg'TRt", | Returtemperatur Energimåler | R | 1 | 1 min
|  |  |  | RT402 | Flow temp Hpu | "338'320'001'TFl402'TSen", |  | R | 1 | 1 min
|  |  |  | RT501 | Flow temp energy Hpu | "338'320'001'MtrEg'TFl", | Turtemperatur Energimåler | R | 1 | 1 min
|  |  |  | RT502 | Return temp Hpu | "338'320'001'TRt502'TSen", |  | R | 1 | 1 min
|  |  |  | OE011 | Active effect energy | "338'320'001'MtrEg'Pwr", | Effekt | R | 2 | 1 min
|  |  |  | OE011 | Cummulated energy heating | "338'320'001'MtrEg'CumEg", | Kumulert energi varme | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'320'001'MtrEg'CumVlm", | Kumulert volum (mengde) | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'320'001'MtrEg'Fl", | StrÃ¸mning | R | 2 | 1 min
|  |  |  | JP501 | Circulation pump command | 338'320'001'Pu501'Cmd | Kommando | R | 2 | 1 min
|  |  |  | JP501 | Circulation pump error | 338'320'001'Pu501'Er | Feil | R | 2 | 1 min
|  |  |  | JP501 | Circulation pump maintenance switch | 338'320'001'Pu501'MntnSwi | Vedlikeholdsbryter | R | 2 | 1 min
|  |  |  | JP502 | Circulation pump command | 338'320'001'Pu502'Cmd | Kommando | R | 2 | 1 min
|  |  |  | JP502 | Circulation pump error | 338'320'001'Pu502'Er | Feil | R | 2 | 1 min
|  |  |  | JP502 | Circulation pump maintenance switch | 338'320'001'Pu502'MntnSwi | Vedlikeholdsbryter | R | 2 | 1 min
|  |  |  | IK001 | COP Virkningsgrad Hpu | "338'320'001'COP'ActvEg1", |  | R | 2 | 1 min
|  |  |  | IK001 | Flow temp Hpu | "338'320'001'Hpu001'Tt", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK001 | Return temp Hpu | "338'320'001'Hpu001'Tr", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK001 | Preset buffertemp Hpu | "338'320'001'Hpu001'Tbt", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK001 | Operation mode | "338'320'001'Hpu001'OpMod", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK001 | Setpoint | "338'320'001'Hpu001'Sp", | Integrert punkt fra maskin | R/W | 1 | 1 min
|  |  |  | IK001 | Hpu alarm | "338'320'001'Hpu001'Alm", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK001 | Compressor op_mode | "338'320'001'Hpu001'OpSta", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK001 | Defrost | "338'320'001'Hpu001'OpStaDf", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK001 | Temperature lower heat source | "338'320'001'Hpu001'TSen", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK001 | Temperature evaporator | "338'320'001'Hpu001'TSenEv", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK001 | Manual mode | "338'320'001'Hpu001'SDOpModMa", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK001 | Temperature ctl | "338'320'001'Hpu001'TCtl", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK001 | Research mode HPU1 | "338'320'001'Forsk'OpModMan1', |  | R | 1 | 1 min
|  |  |  | IK001 | Setpoint Hpu Forskningsdrift | "338'320'001'Forsk'Sp001", |  | R | 1 | 1 min
|  |  |  | IK002 | COP Virkningsgrad Hpu | "338'320'001'COP'ActvEg2", |  | R | 2 | 1 min
|  |  |  | IK002 | Flow temp Hpu | "338'320'001'Hpu002'Tt", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK002 | Return temp Hpu | "338'320'001'Hpu002'Tr", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK002 | Preset buffertemp Hpu | "338'320'001'Hpu002'Tbt", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK002 | Operation mode | "338'320'001'Hpu002'OpMod", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK002 | Setpoint | "338'320'001'Hpu002'Sp", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK002 | Hpu alarm | "338'320'001'Hpu002'Alm", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK002 | Compressor op_mode | "338'320'001'Hpu002'OpSta", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK002 | Defrost | "338'320'001'Hpu002'OpStaDf", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK002 | Temperature lower heat source | "338'320'001'Hpu002'TSen", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK002 | Temperature evaporator | "338'320'001'Hpu002'TSenEv", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK002 | COP Virkningsgrad Hpu | "338'320'001'COP'ActvEg2", | Integrert punkt fra maskin | R | 2 | 1 min
|  |  |  | IK002 | Manual mode | "338'320'001'Hpu002'SDOpModMa", | Integrert punkt fra maskin | R | 0 | 1 min
|  |  |  | IK002 | Temperature ctl | "338'320'001'Hpu002'TCtl", | Integrert punkt fra maskin | R | 1 | 1 min
|  |  |  | IK002 | Research mode HPU2 | "338'320'001'Forsk'OpModMan2', |  | R | 1 | 1 min
|  |  |  | IK002 | Setpoint Hpu Forskningsdrift | "338'320'001'Forsk'Sp002", |  | R | 0 | 1 min
|  |  |  | IK001 | Flow switch | "338'320'001'FlSwi001", |  | R | 0 | 1 min
|  |  |  | IK002 | Flow switch | "338'320'001'FlSwi002", |  | R | 0 | 1 min
|  |  |  | IK001/IK002 | COP Varmepumper | "338'320'001'COP'COP", |  | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart der input | "338'320'001'Char.In", | Inngang | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X1 | "338'320'001'Char.X1", | Knekkpunkt X1 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y1 | "338'320'001'Char.Y1", | Knekkpunkt Y1 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X2 | "338'320'001'Char.X2", | Knekkpunkt X2 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y2 | "338'320'001'Char.Y2", | Knekkpunkt Y2 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X3 | "338'320'001'Char.X3", | Knekkpunkt X3 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y3 | "338'320'001'Char.Y3", | Knekkpunkt Y3 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X4 | "338'320'001'Char.X4", | Knekkpunkt X4 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y4 | "338'320'001'Char.Y4", | Knekkpunkt Y4 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X5 | "338'320'001'Char.X5", | Knekkpunkt X5 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y5 | "338'320'001'Char.Y5", | Knekkpunkt Y5 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X6 | "338'320'001'Char.X6", | Knekkpunkt X6 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y6 | "338'320'001'Char.Y6", | Knekkpunkt Y6 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X7 | "338'320'001'Char.X7", | Knekkpunkt X7 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y7 | "338'320'001'Char.Y7", | Knekkpunkt Y7 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X8 | "338'320'001'Char.X8", | Knekkpunkt X8 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y8 | "338'320'001'Char.Y8", | Knekkpunkt Y8 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X9 | "338'320'001'Char.X9", | Knekkpunkt X9 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y9 | "338'320'001'Char.Y9", | Knekkpunkt Y9 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart X10 | "338'320'001'Char.X10", | Knekkpunkt X10 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart Y10 | "338'320'001'Char.Y10", | Knekkpunkt Y10 | R | 1 | 1 min
|  |  |  | IK001/IK002 | HPU Chart output | "338'320'001'Char.Out", | Utgang | R | 1 | 1 min
| 569115OU001 | 10.205.34.46 | 350806 | RT900 | Outdoor temperature | "338'569'Flr01'RSegm115'TOa", |  | R | 1 | 1 min
Note on E7: Thomas Elvrum Lassen: Stemmer denne merkingen?

## =320.002
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=320.002 | =434-OU001 | 10.205.34.11 | 2443266 | RT007 | PLA-01-E Plate 01, header side, middle-low vertical position | "338'320'002'PCM'TSen007'TSen", |  | R | 1 | 1 min
|  |  |  | RT008 | PCM-01-C Between plates 12 & 13, horizontal middle, down vertical position | "338'320'002'PCM'TSen008'TSen", |  | R | 1 | 1 min
|  |  |  | RT009 | PLA-01-D Plate 01, header side, middle-high vertical position | "338'320'002'PCM'TSen009'TSen", |  | R | 1 | 1 min
|  |  |  | RT010 | PCM-01-A Between plates 12 & 13, horizontal middle, top vertical position | "338'320'002'PCM'TSen010'TSen", |  | R | 1 | 1 min
|  |  |  | RT011 | PCM-01-B Between plates 12 & 13, horizontal middle, middle vertical position | "338'320'002'PCM'TSen011'TSen", |  | R | 1 | 1 min
|  |  |  | RT012 | PLA-01-B Plate 01, turn side, middle vertical position | "338'320'002'PCM'TSen012'TSen", |  | R | 1 | 1 min
|  |  |  | RT013 | PLA-01-A Plate 01, turn side, top vertical position | "338'320'002'PCM'TSen013'TSen", |  | R | 1 | 1 min
|  |  |  | RT014 | PCM-02-A Between plates 01 & 02, turn side, top vertical position | "338'320'002'PCM'TSen014'TSen", |  | R | 1 | 1 min
|  |  |  | RT015 | PLA-01-C Plate 01, turn side, down vertical position | "338'320'002'PCM'TSen015'TSen", |  | R | 1 | 1 min
|  |  |  | RT016 | PCM-02-B Between plates 01 & 02, turn side, middle vertical position | "338'320'002'PCM'TSen016'TSen", |  | R | 1 | 1 min
|  |  |  | RT017 | PCM-02-C Between plates 01 & 02, turn side, down vertical position | "338'320'002'PCM'TSen017'TSen", |  | R | 1 | 1 min
|  |  |  | RT018 | PLA-11-A Plate 11, turn side, top vertical position | "338'320'002'PCM'TSen018'TSen", |  | R | 1 | 1 min
|  |  |  | RT019 | PCM-04-C Between plates 12 & 13, turn side, down vertical position | "338'320'002'PCM'TSen019'TSen", |  | R | 1 | 1 min
|  |  |  | RT020 | PCM-04-A Between plates 12 & 13, turn side, top vertical position | "338'320'002'PCM'TSen020'TSen", |  | R | 1 | 1 min
|  |  |  | RT021 | PCM-04-B Between plates 12 & 13, turn side, middle vertical position | "338'320'002'PCM'TSen021'TSen", |  | R | 1 | 1 min
|  |  |  | RT022 | PCM-03-B Between plates 23 & 24, turn side, middle vertical position | "338'320'002'PCM'TSen022'TSen", |  | R | 1 | 1 min
|  |  |  | RT023 | PCM-03-A Between plates 23 & 24, turn side, top vertical position | "338'320'002'PCM'TSen023'TSen", |  | R | 1 | 1 min
|  |  |  | RT024 | PCM-05-A Between plates 12 & 13, header side, top vertical position | "338'320'002'PCM'TSen024'TSen", |  | R | 1 | 1 min
|  |  |  | RT025 | PLA-24-C Plate 24, turn side, down vertical position | "338'320'002'PCM'TSen025'TSen", |  | R | 1 | 1 min
|  |  |  | RT026 | PCM-05-C Between plates 12 & 13, header side, down vertical position | "338'320'002'PCM'TSen026'TSen", |  | R | 1 | 1 min
|  |  |  | RT027 | PCM-05-B Between plates 12 & 13, header side, middle vertical position | "338'320'002'PCM'TSen027'TSen", |  | R | 1 | 1 min
|  |  |  | RT028 | PCM-03-C Between plates 23 & 24, turn side, down vertical position | "338'320'002'PCM'TSen028'TSen", |  | R | 1 | 1 min
|  |  |  | RT029 | PLA-24-B Plate 24, turn side, middle vertical position | "338'320'002'PCM'TSen029'TSen", |  | R | 1 | 1 min
|  |  |  | RT030 | PLA-24-A Plate 24, turn side, top vertical position | "338'320'002'PCM'TSen030'TSen", |  | R | 1 | 1 min
|  |  |  | RT031 | PLA-24-D Plate 24, header side, middle-high vertical position | "338'320'002'PCM'TSen031'TSen", |  | R | 1 | 1 min
|  |  |  | RT032 | PLA-24-E Plate 24, header side, middle-low vertical position | "338'320'002'PCM'TSen032'TSen", |  | R | 1 | 1 min
|  |  |  | RT033 | OUT-W-B | "338'320'002'PCM'TSen033'TSen", |  | R | 1 | 1 min
|  |  |  | RT034 | OUT-LEFT | "338'320'002'PCM'TSen034'TSen", |  | R | 1 | 1 min
|  |  |  | RT035 | OUT-W-A | "338'320'002'PCM'TSen035'TSen", |  | R | 1 | 1 min
|  |  |  | RT036 | OUT-TOP | "338'320'002'PCM'TSen036'TSen", |  | R | 1 | 1 min
|  |  |  | RT401 | RT401 Temperatur etter fjernvarme | "338'320'002'TFl401'TSen", |  | R | 1 | 1 min
|  |  |  | SB401 | SB401 Ventil "fra system 320.003 inn i PCM system 320.002" | "338'320'002'Vlv401", |  | R | 0 | 1 min
|  |  |  | SB402 | SB402 Ventil "regulerer mot 320.002-SB401 eller retur fjernvarme" | "338'320'002'Vlv402", |  | R | 0 | 1 min
|  |  |  | SB403 | SB403 Ventil "regulerer varme mot 320.003 eller 320.004" | "338'320'002'Vlv403", |  | R | 0 | 1 min
|  |  |  | SB404 | SB404 Ventil "regulerer varme mot topp tank for system 320.001/3 og fra fjernva" | "338'320'002'Vlv404", |  | R | 0 | 1 min
|  |  |  | SB405 | SB405 Ventil "regulerer varme mot topp tank for system 320.001/3 og fra fjernva" | "338'320'002'Vlv405", |  | R | 0 | 1 min
|  |  |  | SB406 | SB406 Ventil PCM- lager 1 | "338'320'002'Vlv406", |  | R | 0 | 1 min
|  |  |  | RD401 | Setpoint Differential pressure | "338'320'002'DP401'Sp", |  | R/W | 3 | 1 min
|  |  |  | RT | PCM Setpoint max temp | "338'320'002'LmMax", |  | R/W | 1 | 1 min
|  |  |  | RT401 | PCM Setpoint | "338'320'002'TFl401'Sp", |  | R/W | 1 | 1 min
|  |  |  | JP401 | Setpoint pump | "338'320'002'SpPuHd", |  | R/W | 0 | 1 min
|  |  |  | RT | PCM average temperature | "338'320'002'PCM'AvrgT", |  | R | 1 | 1 min
|  |  |  | RT | PCM minimum temperature | "338'320'002'PCM'MinT", |  | R | 1 | 1 min
|  |  |  | JP401 | Commando | "338'320'002'Pu401'Cmd", |  | R/W | 0 | 1 min
|  |  |  | SB406 | SB406 Regulator | "338'320'002'Ctrl", |  | R | 0 | 1 min
|  |  |  | RD401 | Differential pressure | "338'320'002'DP401'PSen", |  | R | 3 | 1 min
|  |  |  | OE011 | Cummulated energy heating | "338'320'002'MtrEg'CumEg", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'320'002'MtrEg'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'320'002'MtrEg'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy | "338'320'002'MtrEg'Pwr", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow temp energy | "338'320'002'MtrEg'TFl", |  | R | 2 | 1 min
|  |  |  | OE011 | Return temp energy | "338'320'002'MtrEg'TRt", |  | R | 2 | 1 min
|  |  |  | RT403 | RT401 Turtemperatur etter fjernvarme | "338'320'002'TFl401", |  | R | 1 | 1 min
|  |  |  | RT | PCM Setpoint for Charging | "338'320'OpMod'CtrlPCM'SpInn", |  | R/W | 1 | 1 min
|  |  |  | RT | PCM Setpoint for discharge | "338'320'OpMod'CtrlPCM'SpOut", |  | R/W | 1 | 1 min
|  |  |  | RT | PCM Highest temperature | "338'320'OpMod'CtrlPCM'TSenHigh", |  | R | 1 | 1 min
|  |  |  | XS001 | PCM Operation mode | "338'320'OpMod'OpMod", |  | R | 0 | 1 min
|  |  |  | XS002 | PCM Operation mode manual | "338'320'OpMod'OpModMan2", |  | R | 0 | 1 min

## =320.003
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=320.003 | =434-OU004 | 10.205.34.17 | 2443270 | OE014 | Cummulated energy heating | "338'320'003'Mtr14'CumEg", |  | R | 2 | 1 min
|  |  |  | OE014 | Cummulated volume m3 | "338'320'003'Mtr14'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE014 | Flow l/h | "338'320'003'Mtr14'Fl", |  | R | 2 | 1 min
|  |  |  | OE014 | Active effect energy | "338'320'003'Mtr14'Pwr", |  | R | 2 | 1 min
|  |  |  | OE014 | Flow temp energy | "338'320'003'Mtr14'TFl", |  | R | 1 | 1 min
|  |  |  | OE014 | Return temp energy | "338'320'003'Mtr14'TRt", |  | R | 1 | 1 min
|  |  |  | OE015 | Cummulated energy heating | "338'320'003'Mtr15'CumEg", |  | R | 2 | 1 min
|  |  |  | OE015 | Cummulated volume m3 | "338'320'003'Mtr15'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE015 | Flow l/h | "338'320'003'Mtr15'Fl", |  | R | 2 | 1 min
|  |  |  | OE015 | Active effect energy | "338'320'003'Mtr15'Pwr", |  | R | 2 | 1 min
|  |  |  | OE015 | Flow temp energy | "338'320'003'Mtr15'TFl", |  | R | 1 | 1 min
|  |  |  | OE015 | Return temp energy | "338'320'003'Mtr15'TRt", |  | R | 1 | 1 min
+338=320.003 | =434-OU002 | 10.205.34.12 | 2443265 | OE016 | Cummulated energy heating | "338'320'003'MtrH16'CumEg", |  | R | 2 | 1 min
|  |  |  | OE016 | Cummulated volume m3 | "338'320'003'MtrH16'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE016 | Flow l/h | "338'320'003'MtrH16'Fl", |  | R | 2 | 1 min
|  |  |  | OE016 | Active effect energy | "338'320'003'MtrH16'Pwr", |  | R | 2 | 1 min
|  |  |  | OE016 | Flow temp energy | "338'320'003'MtrH16'TFl", |  | R | 1 | 1 min
|  |  |  | OE016 | Return temp energy | "338'320'003'MtrH16'TRt", |  | R | 1 | 1 min
|  |  |  | OE017 | Cummulated energy heating | "338'320'003'MtrH17'CumEg", |  | R | 2 | 1 min
|  |  |  | OE017 | Cummulated volume m3 | "338'320'003'MtrH17'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE017 | Flow l/h | "338'320'003'MtrH17'Fl", |  | R | 2 | 1 min
|  |  |  | OE017 | Active effect energy | "338'320'003'MtrH17'Pwr", |  | R | 2 | 1 min
|  |  |  | OE017 | Flow temp energy | "338'320'003'MtrH17'TFl", |  | R | 1 | 1 min
|  |  |  | OE017 | Return temp energy | "338'320'003'MtrH17'TRt", |  | R | 1 | 1 min
|  |  |  | OE013 | Cummulated energy heating | "338'320'003'MtrH13'CumEg", |  | R | 2 | 1 min
|  |  |  | OE013 | Cummulated volume m3 | "338'320'003'MtrH13'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE013 | Flow l/h | "338'320'003'MtrH13'Fl", |  | R | 2 | 1 min
|  |  |  | OE013 | Active effect energy | "338'320'003'MtrH13'Pwr", |  | R | 2 | 1 min
|  |  |  | OE013 | Flow temp energy | "338'320'003'MtrH13'TFl", |  | R | 1 | 1 min
|  |  |  | OE013 | Return temp energy | "338'320'003'MtrH13'TRt", |  | R | 1 | 1 min
+338=320.003 | =434-OU001 | 10.205.34.11 | 2443266 | RD401 | Differential pressure | "338'320'003'DP401'PSen", |  | R | 1 | 1 min
|  |  |  | RP401 | Pressure exp | "338'320'003'DPMon501'PSen", |  | R | 1 | 1 min
|  |  |  | RT401 | Temp flow district heating | "338'320'003'TFl401'TSen", |  | R | 1 | 1 min
|  |  |  | RT402 | Temp flow buffer tank | "338'320'003'TFl402'TSen", |  | R | 1 | 1 min
|  |  |  | RT501 | Temp return to buffertank | "338'320'003'TRt501'TSen", |  | R | 1 | 1 min
|  |  |  | RT502 | Temp return ventilation | "338'320'003'TRt502'TSen", |  | R | 1 | 1 min
|  |  |  | RT507 | Temp return radiators | "338'320'003'TRt507'TSen", |  | R | 1 | 1 min
|  |  |  | RT508 | Temp return radiator & batt research cells | "338'320'003'TRt508'TSen", |  | R | 1 | 1 min
|  |  |  | JP401 | Energy consum | "338'320'003'PuTwn'Pu401'GruInt'EgCns", |  | R | 2 | 1 min
|  |  |  | JP401 | Flowrate | "338'320'003'PuTwn'Pu401'GruInt'FlRate", |  | R | 2 | 1 min
|  |  |  | JP401 | Pressure | "338'320'003'PuTwn'Pu401'GruInt'PuHd", |  | R | 2 | 1 min
|  |  |  | JP401 | Output | "338'320'003'PuTwn'Pu401'GruInt'PuOut", |  | R | 0 | 1 min
|  |  |  | JP401 | Speed | "338'320'003'PuTwn'Pu401'GruInt'PuSpd", |  | R | 2 | 1 min
|  |  |  | JP401 | Temp flow | "338'320'003'PuTwn'Pu401'GruInt'TFl", |  | R | 1 | 1 min
|  |  |  | JP402 | Energy consum | "338'320'003'PuTwn'Pu402'GruInt'EgCns", |  | R | 2 | 1 min
|  |  |  | JP402 | Flowrate | "338'320'003'PuTwn'Pu402'GruInt'FlRate", |  | R | 2 | 1 min
|  |  |  | JP402 | Pressure | "338'320'003'PuTwn'Pu402'GruInt'PuHd", |  | R | 1 | 1 min
|  |  |  | JP402 | Output | "338'320'003'PuTwn'Pu402'GruInt'PuOut", |  | R | 0 | 1 min
|  |  |  | JP402 | Speed | "338'320'003'PuTwn'Pu402'GruInt'PuSpd", |  | R | 1 | 1 min
|  |  |  | JP402 | Temp flow | "338'320'003'PuTwn'Pu402'GruInt'TFl", |  | R | 1 | 1 min
|  |  |  | OE012 | Cummulated energy heating | "338'320'003'MtrEg'CumEg", |  | R | 2 | 1 min
|  |  |  | OE012 | Cummulated volume m3 | "338'320'003'MtrEg'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE012 | Flow l/h | "338'320'003'MtrEg'Fl", |  | R | 2 | 1 min
|  |  |  | OE012 | Active effect energy | "338'320'003'MtrEg'Pwr", |  | R | 2 | 1 min
|  |  |  | OE012 | Flow temp energy | "338'320'003'MtrEg'TFl", |  | R | 1 | 1 min
|  |  |  | OE012 | Return temp energy | "338'320'003'MtrEg'TRt", |  | R | 1 | 1 min
|  |  |  | OE011 | Cummulated energy heating | "338'320'003'MtrEg1'CumEg", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'320'003'MtrEg1'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'320'003'MtrEg1'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy | "338'320'003'MtrEg1'Pwr", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow temp energy | "338'320'003'MtrEg1'TFl", |  | R | 1 | 1 min
|  |  |  | OE011 | Return temp energy | "338'320'003'MtrEg1'TRt", |  | R | 1 | 1 min
|  |  |  | DP401 | Setpoint Differential pressure | "338'320'003'DP401'Sp", |  | R | 1 | 1 min
|  |  |  | JP401 | Setpoint pressure | "338'320'003'SpP", |  | R | 1 | 1 min
|  |  |  | RT401 | Setpoint temp flow | "338'320'003'TFl401'Sp", |  | R | 1 | 1 min
|  |  |  | RT402 | Setpoint temp flow | "338'320'003'TFl402'Sp", |  | R | 1 | 1 min
|  |  |  | RT900 | Setpoint temp heatcable | "338'320'003'Sp", |  | R | 1 | 1 min
|  |  |  | LZ001 | Output heating cable | "338'320'003'ElH", |  | R | 0 | 1 min
|  |  |  | SB501 | Radiator valve Forskercelle1 | "338'569'219'TCtl'Vlv", |  | R | 0 | 1 min
|  |  |  | SB502 | Radiator valve Forskercelle2 | "338'569'220'TCtl'Vlv", |  | R | 0 | 1 min

## =320.004
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=320.004 | =434-OU001 | 10.205.34.11 | 2443266 | OE010 | Cummulated energy heating | "338'320'004'MtrEg'CumEg", |  | R | 2 | 1 min
|  |  |  | OE010 | Cummulated volume m3 | "338'320'004'MtrEg'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE010 | Flow l/h | "338'320'004'MtrEg'Fl", |  | R | 2 | 1 min
|  |  |  | OE010 | Active effect energy | "338'320'004'MtrEg'Pwr", |  | R | 2 | 1 min
|  |  |  | RT401 | Flow temp energy | "338'320'004'MtrEg'TFl", |  | R | 1 | 1 min
|  |  |  | RT501 | Return temp energy | "338'320'004'MtrEg'TRt", |  | R | 1 | 1 min
|  |  |  | SB501 | Valve heating building | "338'320'004'HExg401'VlvPrim", |  | R | 0 | 1 min
|  |  |  | SB502 | Valve PCM heating | "338'320'004'HExg402'VlvPrim", |  | R | 0 | 1 min
|  |  |  | X | Knekkpunkt X1 | "338'320'004'HExg401'Char.X1", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y1 | "338'320'004'HExg401'Char.Y1", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X2 | "338'320'004'HExg401'Char.X2", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y2 | "338'320'004'HExg401'Char.Y2", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X3 | "338'320'004'HExg401'Char.X3", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y3 | "338'320'004'HExg401'Char.Y3", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X4 | "338'320'004'HExg401'Char.X4", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y4 | "338'320'004'HExg401'Char.Y4", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X5 | "338'320'004'HExg401'Char.X5", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y5 | "338'320'004'HExg401'Char.Y5", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X6 | "338'320'004'HExg401'Char.X6", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y6 | "338'320'004'HExg401'Char.Y6", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X7 | "338'320'004'HExg401'Char.X7", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y7 | "338'320'004'HExg401'Char.Y7", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X8 | "338'320'004'HExg401'Char.X8", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y8 | "338'320'004'HExg401'Char.Y8", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X9 | "338'320'004'HExg401'Char.X9", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y9 | "338'320'004'HExg401'Char.Y9", |  | R | 1 | 1 min
|  |  |  | X | Knekkpunkt X10 | "338'320'004'HExg401'Char.X10", |  | R | 1 | 1 min
|  |  |  | Y | Knekkpunkt Y10 | "338'320'004'HExg401'Char.Y10", |  | R | 1 | 1 min
|  |  |  | SB502 | Setpoint Valve PCM heating | "338'320'004'HExg402'SpH", |  | R | 1 | 1 min
| 569115OU001 | 10.205.34.46 | 350806 | RT900 | Outdoor temperature | "338'569'Flr01'RSegm115'TOa", |  | R | 1 | 1 min

## =360.001
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=360.001 | =434-OU003 | 10.205.34.16 | 2443267 | XS0001 | Switch Operation mode | "338'360'001'OpModSwi", |  | R/W | 0 | 1 min
|  |  |  | XS0001 | Manual Operation mode | "338'360'001'OpModMan", |  | R/W | 0 | 1 min
|  |  |  | XS0001 | Current Operation mode | "338'360'001'PrOpMod", |  | R/W | 0 | 1 min
|  |  |  | RT422 | Heat coil temp flow | "338'360'001'PreHcl'TFl", |  | R | 1 | 1 min
|  |  |  | RT521 | Heat coil temp return | "338'360'001'PreHcl'TRt", |  | R | 1 | 1 min
|  |  |  | RT421 | Flow temp energy | "338'360'001'Mtr11'TFl", |  | R | 1 | 1 min
|  |  |  | RT522 | Return temp energy | "338'360'001'Mtr11'TRt", |  | R | 1 | 1 min
|  |  |  | SB521 | Heat coil valve | "338'360'001'PreHcl'Vlv", |  | R | 0 | 1 min
|  |  |  | JP421 | Heat coil pump | "338'360'001'PreHcl'Pu'Cmd", |  | R | 0 | 1 min
|  |  |  | JP421 | Heat coil pump status | "338'360'001'PreHcl'Pu'KickFnct.OpSta", |  | R | 0 | 1 min
+338=360.001 | =434-OU004 | 10.205.34.17 | 2443270 | OE011 | Cummulated energy heating | "338'360'001'Mtr11'CumEg", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'360'001'Mtr11'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'360'001'Mtr11'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy | "338'360'001'Mtr11'Pwr", |  | R | 2 | 1 min
+338=360.001 | =434-OU003 | 10.205.34.16 | 2443267 | RT401 | Inlet duct temp | "338'360'001'TOaDct1'TSen", |  | R | 1 | 1 min
|  |  |  | KA401 | Damper inlet | "338'360'001'DmpShofEh'Cmd1", |  | R | 0 | 1 min
|  |  |  | QD401 | Diff pressure filter inlet | "338'360'001'FilOa", |  | R | 1 | 1 min
|  |  |  | QR401 | Heatexchanger rotation monitor | "338'360'001'Erc'ErcMon", |  | R | 0 | 1 min
|  |  |  | LX401 | Heatexchanger effiecency | "338'360'001'Erc'ErcMon'Efcy", |  | R | 2 | 1 min
|  |  |  | LX401 | Heatexchanger percent | "338'360'001'Erc'Mot'Mdlt", |  | R | 0 | 1 min
|  |  |  | RT402 | Duct temp after heatexchanger supply | "338'360'001'Erc'ErcMon'TAfErc", |  | R | 1 | 1 min
|  |  |  | RD401 | Diff pressure Supply fan | "338'360'001'FanSu'DP", |  | R | 1 | 1 min
|  |  |  | JV401 | Supply air fan commando | "338'360'001'FanSu'Cmd", |  | R | 0 | 1 min
|  |  |  | JV401 | Supply air fan volume | "338'360'001'FanSu'VlmC'VlmFl", |  | R | 2 | 1 min
|  |  |  | QT401 | Supply air temp watch | "338'360'001'PreHcl'FrPrtMon", |  | R | 1 | 1 min
|  |  |  | RT410 | Duct temp after heatcoil | "338'360'001'TSu'TSen", |  | R | 1 | 1 min
|  |  |  | RT410 | Setpoint supply air temperature | "338'360'001'PrSp", |  | R | 1 | 1 min
|  |  |  | RP401 | Pressure sensor supply air | "338'360'001'FanSu'DPMon'PSen", |  | R | 1 | 1 min
|  |  |  | RP401 | Setpoint pressure sensor supply air | "338'360'001'FanSu'FanOpti1'PrSpP", |  | R | 1 | 1 min
|  |  |  | SQxxx | Setpoint VAV | "338'360'001'FanSu'FanOpti1'SpVavAng", |  | R | 0 | 1 min
|  |  |  | RY401 | Smoke detector supply air | "338'360'001'SmextSu", |  | R | 0 | 1 min
|  |  |  | RD502 | Diff pressure extract air fan add. | "338'360'001'FanEx1'DP", |  | R | 1 | 1 min
|  |  |  | JV502 | Extract air fan commando add. | "338'360'001'FanEx1'Cmd", |  | R | 0 | 1 min
|  |  |  | RY501 | Smoke detector extract air | "338'360'001'SmextEh", |  | R | 0 | 1 min
|  |  |  | RP501 | Pressure sensor extract air | "338'360'001'FanEx'DPMon2'PSen", |  | R | 1 | 1 min
|  |  |  | RT501 | Extract air temp | "338'360'001'TEx'TSen", |  | R | 1 | 1 min
|  |  |  | QD401 | Diff pressure filter extract air | "338'360'001'FilEx", |  | R | 1 | 1 min
|  |  |  | RT502 | Duct temp after heatexchanger extract | "338'360'001'TEh'TSen", |  | R | 1 | 1 min
|  |  |  | RD501 | Diff pressure extract air fan | "338'360'001'FanEx'DP", |  | R | 1 | 1 min
|  |  |  | JV501 | Extract air fan commando | "338'360'001'FanEx'Cmd", |  | R | 0 | 1 min
|  |  |  | JV501 | Extract air volume | "338'360'001'FanEx'VlmC'VlmFl", |  | R | 2 | 1 min
|  |  |  | KA501 | Damper exhaust | "338'360'001'DmpShofEh'Cmd1", |  | R | 0 | 1 min
|  |  |  | JV401 | Calculated SFP | "338'360'001'FanSu'FlCalc'Fac", |  | R | 2 | 1 min
|  |  |  | RT900 | Utetemperatur | "338'360'001'TOa", |  | R | 1 | 1 min

## =360.002
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=360.002 | =434-OU003 | 10.205.34.16 | 2443267 | XS0001 | Switch Operation mode | "338'360'002'OpModSwi", |  | R/W | 0 | 1 min
|  |  |  | XS0001 | Manual Operation mode | "338'360'002'OpModMan", |  | R/W | 0 | 1 min
|  |  |  | XS0001 | Current Operation mode | "338'360'002'PrOpMod", |  | R/W | 0 | 1 min
|  |  |  | RT422 | Heat coil temp flow | "338'360'002'PreHcl'TFl", |  | R | 1 | 1 min
|  |  |  | RT521 | Heat coil temp return | "338'360'002'PreHcl'TRt", |  | R | 1 | 1 min
|  |  |  | RT421 | Flow temp energy | "338'360'002'Mtr11'TFl", |  | R | 1 | 1 min
|  |  |  | RT522 | Return temp energy | "338'360'002'Mtr11'TRt", |  | R | 1 | 1 min
|  |  |  | SB521 | Heat coil valve | "338'360'002'PreHcl'Vlv", |  | R | 0 | 1 min
|  |  |  | JP421 | Heat coil pump | "338'360'002'PreHcl'Pu'Cmd", |  | R | 0 | 1 min
|  |  |  | JP421 | Heat coil pump status | "338'360'002'PreHcl'Pu'KickFnct.OpSta", |  | R | 0 | 1 min
| =434-OU004 | 10.205.34.17 | 2443270 | OE011 | Cummulated energy heating | "338'360'002'Mtr11'CumEg", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'360'002'Mtr11'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'360'002'Mtr11'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy | "338'360'002'Mtr11'Pwr", |  | R | 2 | 1 min
| =434-OU003 | 10.205.34.16 | 2443267 | RT401 | Inlet duct temp | "338'360'002'TOaDct1'TSen", |  | R | 1 | 1 min
|  |  |  | KA401 | Damper inlet | "338'360'002'DmpShofEh'Cmd1", |  | R | 0 | 1 min
|  |  |  | QD401 | Diff pressure filter inlet | "338'360'002'FilOa", |  | R | 1 | 1 min
|  |  |  | QR401 | Heatexchanger rotation monitor | "338'360'002'Erc'ErcMon", |  | R | 0 | 1 min
|  |  |  | LX401 | Heatexchanger effiecency | "338'360'002'Erc'ErcMon'Efcy", |  | R | 2 | 1 min
|  |  |  | LX401 | Heatexchanger percent | "338'360'002'Erc'Mot'Mdlt", |  | R | 0 | 1 min
|  |  |  | RT402 | Duct temp after heatexchanger supply | "338'360'002'Erc'ErcMon'TAfErc", |  | R | 1 | 1 min
|  |  |  | RD401 | Diff pressure Supply fan | "338'360'002'FanSu'DP", |  | R | 1 | 1 min
|  |  |  | JV401 | Supply air fan commando | "338'360'002'FanSu'Cmd", |  | R | 0 | 1 min
|  |  |  | JV401 | Supply air fan volume | "338'360'002'FanSu'VlmC'VlmFl", |  | R | 2 | 1 min
|  |  |  | QT401 | Supply air temp watch | "338'360'002'PreHcl'FrPrtMon", |  | R | 1 | 1 min
|  |  |  | RT410 | Duct temp after heatcoil | "338'360'002'TSu'TSen", |  | R | 1 | 1 min
|  |  |  | RT410 | Setpoint supply air temperature | "338'360'002'PrSp", |  | R | 1 | 1 min
|  |  |  | RP401 | Pressure sensor supply air | "338'360'002'FanSu'DPMon'PSen", |  | R | 1 | 1 min
|  |  |  | RP401 | Setpoint pressure sensor supply air | "338'360'002'FanSu'FanOpti1'PrSpP", |  | R | 1 | 1 min
|  |  |  | SQxxx | Setpoint VAV | "338'360'002'FanSu'FanOpti1'SpVavAng", |  | R | 0 | 1 min
|  |  |  | RY401 | Smoke detector supply air | "338'360'002'SmextSu", |  | R | 0 | 1 min
|  |  |  | RD502 | Diff pressure extract air fan add. | "338'360'002'FanEx1'DP", |  | R | 1 | 1 min
|  |  |  | JV502 | Extract air fan commando add. | "338'360'002'FanEx1'Cmd", |  | R | 0 | 1 min
|  |  |  | RY501 | Smoke detector extract air | "338'360'002'SmextEh", |  | R | 0 | 1 min
|  |  |  | RP501 | Pressure sensor extract air | "338'360'002'FanEx'DPMon2'PSen", |  | R | 1 | 1 min
|  |  |  | RT501 | Extract air temp | "338'360'002'TEx'TSen", |  | R | 1 | 1 min
|  |  |  | QD401 | Diff pressure filter extract air | "338'360'002'FilEx", |  | R | 1 | 1 min
|  |  |  | RT502 | Duct temp after heatexchanger extract | "338'360'002'TEh'TSen", |  | R | 1 | 1 min
|  |  |  | RD501 | Diff pressure extract air fan | "338'360'002'FanEx'DP", |  | R | 1 | 1 min
|  |  |  | JV501 | Extract air fan commando | "338'360'002'FanEx'Cmd", |  | R | 0 | 1 min
|  |  |  | JV501 | Extract air volume | "338'360'002'FanEx'VlmC'VlmFl", |  | R | 2 | 1 min
|  |  |  | KA501 | Damper exhaust | "338'360'002'DmpShofEh'Cmd1", |  | R | 0 | 1 min
|  |  |  | JV401 | Calculated SFP | "338'360'002'FanSu'FlCalc'Fac", |  | R | 2 | 1 min

## =360.003
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=360.003 | =434-OU002 | 10.205.34.12 | 2443265 | RT432 | Flow temp Cooling coil | "338'360'003'Ccl'TFl", |  | R | 1 | 1 min
|  |  |  | RT531 | Return temp Cooling coil | "338'360'003'Ccl'TRt", |  | R | 1 | 1 min
|  |  |  | RT422 | Flow temp Heating coil | "338'360'003'PreHcl'TFl", |  | R | 1 | 1 min
|  |  |  | RT521 | Return temp Heating coil | "338'360'003'PreHcl'TRt", |  | R | 1 | 1 min
|  |  |  | RD501 | Diff pressure extract air fan | "338'360'003'FanEx'DP", |  | R | 1 | 1 min
|  |  |  | RP501 | Pressure sensor extract air | "338'360'003'FanEx'PSen", |  | R | 1 | 1 min
|  |  |  | RD401 | Diff pressure supply air fan | "338'360'003'FanSu'DP", |  | R | 1 | 1 min
|  |  |  | RP401 | Pressure sensor inlet air | "338'360'003'FanSu'PSen", |  | R | 1 | 1 min
|  |  |  | RP402 | Pressure sensor supply air | "338'360'003'FanSu'PSen1", |  | R | 1 | 1 min
|  |  |  | RP421 | Pressure sensor | "338'569'220'Psen", |  | R | 1 | 1 min
|  |  |  | RH401 | Relative hum supply air | "338'360'003'HuRel", |  | R | 0 | 1 min
|  |  |  | RH501 | Relative hum extract air | "338'360'003'HuRel1", |  | R | 0 | 1 min
|  |  |  | RT900 | Utetemperatur | "338'360'001'TOa", |  | R | 1 | 1 min
|  |  |  | RT401 | Temp sens supply after cool coil | "338'360'003'TSu", |  | R | 1 | 1 min
|  |  |  | RT402 | Temp sens supply after heat coil | "338'360'003'TSu1", |  | R | 1 | 1 min
|  |  |  | RT403 | Temp sens supply after electric heat coil | "338'360'003'TSu2", |  | R | 1 | 1 min
|  |  |  | JV501 | Maintenance switch | "338'360'003'FanEx'MntnSwi", |  | R | 0 | 1 min
|  |  |  | JV501 | State | "338'360'003'FanEx'Cmd", |  | R/W | 0 | 1 min
|  |  |  | JV501 | Command value | "338'360'003'FanEx'Mdlt", |  | R/W | 0 | 1 min
|  |  |  | JV501 | Air volume flow m3/h | "338'360'003'FanEx'AirVlmFl", |  | R | 1 | 1 min
|  |  |  | JV501 | Setpoint air volume flow | "338'360'003'FanEx'SpAfl", |  | R/W | 0 | 1 min
|  |  |  | JV401 | Setpoint Max airflow | "338'360'003'FanSu'Sp1", |  | R/W | 0 | 1 min
|  |  |  | JV401 | Setpoint Min airflow | "338'360'003'FanSu'Sp2", |  | R/W | 0 | 1 min
|  |  |  | JV401 | K-Faktor till. | "338'360'003'FanSu'VlmC'KFakct", |  | R | 2 | 1 min
|  |  |  | JV401 | Air volume flow m3/h | "338'360'003'FanSu'VlmC'VlmFl", |  | R/W | 2 | 1 min
|  |  |  | JV401 | Command value | "338'360'003'FanSu'Mdlt", |  | R/W | 0 | 1 min
|  |  |  | JV401 | State | "338'360'003'FanSu'Cmd", |  | R/W | 0 | 1 min
|  |  |  | JV401 | Kommando | "338'360'003'FanSu'DfsInt'Cmd", |  | R | 0 | 1 min
|  |  |  | JV401 | Error indication | "338'360'003'FanSu'DfsInt'FltInd", |  | R | 0 | 1 min
|  |  |  | JV401 | Supply fan error | "338'360'003'FanSu'Er", |  | R | 0 | 1 min
|  |  |  | JV401 | Maintenance switch | "338'360'003'FanSu'MntnSwi", |  | R | 0 | 1 min
|  |  |  | JV401 | Cummulated energy | "338'360'003'FanSu'DfsInt'CumEg", |  | R | 2 | 1 min
|  |  |  | JV401 | Current | "338'360'003'FanSu'DfsInt'Curr", |  | R | 2 | 1 min
|  |  |  | JV401 | Error code | "338'360'003'FanSu'DfsInt'FltCode", |  | R | 0 | 1 min
|  |  |  | JV401 | Counter operating hours | "338'360'003'FanSu'DfsInt'PrOph", |  | R | 0 | 1 min
|  |  |  | JV401 | Active effect | "338'360'003'FanSu'DfsInt'Pwr", |  | R | 2 | 1 min
|  |  |  | JV401 | Warning code | "338'360'003'FanSu'DfsInt'WarnCode", |  | R | 0 | 1 min
|  |  |  | OE012 | Cummulated energy cool | "338'360'003'Ccl'MtrC'CumEgC", |  | R | 2 | 1 min
|  |  |  | OE012 | Cummulated volume m3 | "338'360'003'Ccl'MtrC'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE012 | Flow l/h | "338'360'003'Ccl'MtrC'Fl", |  | R | 2 | 1 min
|  |  |  | OE012 | Active effect energy cool | "338'360'003'Ccl'MtrC'Pwr", |  | R | 2 | 1 min
|  |  |  | OE012 | Flow temp energy cool | "338'360'003'Ccl'MtrC'TFl", |  | R | 1 | 1 min
|  |  |  | OE012 | Return temp energy cool | "338'360'003'Ccl'MtrC'TRt", |  | R | 1 | 1 min
|  |  |  | OE011 | Cummulated energy heat | "338'360'003'PreHcl'MtrH'CumEg", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'360'003'PreHcl'MtrH'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'360'003'PreHcl'MtrH'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy heat | "338'360'003'PreHcl'MtrH'Pwr", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow temp energy | "338'360'003'PreHcl'MtrH'TFl", |  | R | 1 | 1 min
|  |  |  | OE011 | Return temp energy | "338'360'003'PreHcl'MtrH'TRt", |  | R | 1 | 1 min
|  |  |  | SB531 | Valve cooling coil | "338'360'003'Ccl'Vlv", |  | R/W | 0 | 1 min
|  |  |  | SB521 | Valve Heating coil | "338'360'003'PreHcl'Vlv", |  | R/W | 0 | 1 min
|  |  |  | RT603 | Actual cool setpoint | "338'360'003'PrSp", |  | R/W | 1 | 1 min
|  |  |  | RT603 | Actual heat setpoint | "338'360'003'PrSp1", |  | R/W | 1 | 1 min
|  |  |  | RT403 | Max setpoint heat air supply | "338'360'003'SpSuMaxH", |  | R/W | 1 | 1 min
|  |  |  | RY401 | Fire detector supply air | "338'360'003'FireDet", |  | R | 0 | 1 min
|  |  |  | LV402 | Maintenance switch | "338'360'003'HclEl'MntnSwi", |  | R | 0 | 1 min
|  |  |  | LV402 | Temperature over alarm | "338'360'003'HclEl'TOvr", |  | R | 0 | 1 min
|  |  |  | LV402 | Command onoff | "338'360'003'HclEl'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | LV402 | Command value | "338'360'003'HclEl'StSwi'Mdlt", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Pump error | "338'360'003'PreHcl'Pu'Er", |  | R | 0 | 1 min
|  |  |  | JP421 | Maintenance switch | "338'360'003'PreHcl'Pu'MntnSwi", |  | R | 0 | 1 min
|  |  |  | JP421 | Pump command | "338'360'003'PreHcl'Pu'Cmd", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Enable kick function mosjonering | "338'360'003'PreHcl'Pu'KickFnct.EnFnct", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Reset kick function mosjonering | "338'360'003'PreHcl'Pu'KickFnct.Reset", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Kick function Operation state mosjonering | "338'360'003'PreHcl'Pu'KickFnct.OpSta", |  | R | 0 | 1 min
|  |  |  | JP421 | Kick function output mosjonering | "338'360'003'PreHcl'Pu'KickFnct.Out", |  | R | 0 | 1 min
|  |  |  | KA502 | Damper extract air | "338'360'003'DmpShofEx'Cmd1", |  | R/W | 0 | 1 min
|  |  |  | KA502 | Command value | "338'360'003'DmpShofEx'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | KA401 | Damper supply air | "338'360'003'DmpShofOa'Cmd1", |  | R/W | 0 | 1 min
|  |  |  | KA401 | Command value | "338'360'003'DmpShofOa'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | LK401 | Command value cool | "338'360'003'Ccl'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | LK401 | ManOpSel cooling coil | "338'360'003'SqCtr'CclManOp", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LV402 | ManOpSel El coil | "338'360'003'SqCtr'EclManOp", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LV401 | ManOpSel Heating coil | "338'360'003'SqCtr'HclManMod", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LV403 | ManOpSel Radiator | "338'360'003'SqCtr'RadManOp", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LC001 | ManOpSel cool pump | "338'360'003'OpModSwi", |  | R/W | 0 | 1 min
|  |  |  | XS0001 | Plant control | "338'360'003'OpModMan", |  | R/W | 0 | 1 min | Av | Forskningsdrift
|  |  |  | XS0002 | Control heating seq | "338'360'003'OpModMan1", |  | R/W | 0 | 1 min | Alle varmesekvenser | Varmebehov 1 uten elvarme

## =360.004
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=360.003 | =434-OU002 | 10.205.34.12 | 2443265 | RT432 | Flow temp Cooling coil | "338'360'004'Ccl'TFl", |  | R | 1 | 1 min
|  |  |  | RT531 | Return temp Cooling coil | "338'360'004'Ccl'TRt", |  | R | 1 | 1 min
|  |  |  | RT422 | Flow temp Heating coil | "338'360'004'PreHcl'TFl", |  | R | 1 | 1 min
|  |  |  | RT521 | Return temp Heating coil | "338'360'004'PreHcl'TRt", |  | R | 1 | 1 min
|  |  |  | RD501 | Diff pressure extract air fan | "338'360'004'FanEx'DP", |  | R | 1 | 1 min
|  |  |  | RP501 | Pressure sensor extract air | "338'360'004'FanEx'PSen", |  | R | 1 | 1 min
|  |  |  | RD401 | Diff pressure supply air fan | "338'360'004'FanSu'DP", |  | R | 1 | 1 min
|  |  |  | RP401 | Pressure sensor inlet air | "338'360'004'FanSu'PSen", |  | R | 1 | 1 min
|  |  |  | RP402 | Pressure sensor supply air | "338'360'004'FanSu'PSen1", |  | R | 1 | 1 min
|  |  |  | RP421 | Pressure sensor | "338'569'219'Psen", |  | R | 1 | 1 min
|  |  |  | RH401 | Relative hum supply air | "338'360'004'HuRel", |  | R | 0 | 1 min
|  |  |  | RH501 | Relative hum extract air | "338'360'004'HuRel1", |  | R | 0 | 1 min
|  |  |  | RT900 | Utetemperatur | "338'360'004'TOa", |  | R | 1 | 1 min
|  |  |  | RT401 | Temp sens supply after cool coil | "338'360'004'TSu", |  | R | 1 | 1 min
|  |  |  | RT402 | Temp sens supply after heat coil | "338'360'004'TSu1", |  | R | 1 | 1 min
|  |  |  | RT403 | Temp sens supply after electric heat coil | "338'360'004'TSu2", |  | R | 1 | 1 min
|  |  |  | JV501 | Maintenance switch | "338'360'004'FanEx'MntnSwi", |  | R | 0 | 1 min
|  |  |  | JV501 | State | "338'360'004'FanEx'Cmd", |  | R/W | 0 | 1 min
|  |  |  | JV501 | Command value | "338'360'004'FanEx'Mdlt", |  | R/W | 0 | 1 min
|  |  |  | JV501 | Air volume flow m3/h | "338'360'004'FanEx'AirVlmFl", |  | R | 1 | 1 min
|  |  |  | JV501 | Setpoint air volume flow | "338'360'004'FanEx'SpAfl", |  | R/W | 0 | 1 min
|  |  |  | JV401 | Setpoint Max airflow | "338'360'004'FanSu'Sp1", |  | R/W | 0 | 1 min
|  |  |  | JV401 | Setpoint Min airflow | "338'360'004'FanSu'Sp2", |  | R/W | 0 | 1 min
|  |  |  | JV401 | K-Faktor till. | "338'360'004'FanSu'VlmC'KFakct", |  | R | 2 | 1 min
|  |  |  | JV401 | Air volume flow m3/h | "338'360'004'FanSu'VlmC'VlmFl", |  | R/W | 2 | 1 min
|  |  |  | JV401 | Command value | "338'360'004'FanSu'Mdlt", |  | R/W | 0 | 1 min
|  |  |  | JV401 | State | "338'360'004'FanSu'Cmd", |  | R/W | 0 | 1 min
|  |  |  | JV401 | Command | "338'360'004'FanSu'DfsInt'Cmd", |  | R | 0 | 1 min
|  |  |  | JV401 | Error indication | "338'360'004'FanSu'DfsInt'FltInd", |  | R | 0 | 1 min
|  |  |  | JV401 | Supply fan error | "338'360'004'FanSu'Er", |  | R | 0 | 1 min
|  |  |  | JV401 | Maintenance switch | "338'360'004'FanSu'MntnSwi", |  | R | 0 | 1 min
|  |  |  | JV401 | Cummulated energy | "338'360'004'FanSu'DfsInt'CumEg", |  | R | 2 | 1 min
|  |  |  | JV401 | Current | "338'360'004'FanSu'DfsInt'Curr", |  | R | 2 | 1 min
|  |  |  | JV401 | Error code | "338'360'004'FanSu'DfsInt'FltCode", |  | R | 0 | 1 min
|  |  |  | JV401 | Counter operating hours | "338'360'004'FanSu'DfsInt'PrOph", |  | R | 0 | 1 min
|  |  |  | JV401 | Active effect | "338'360'004'FanSu'DfsInt'Pwr", |  | R | 2 | 1 min
|  |  |  | JV401 | Warning code | "338'360'004'FanSu'DfsInt'WarnCode", |  | R | 0 | 1 min
|  |  |  | OE012 | Cummulated energy cool | "338'360'004'Ccl'MtrC'CumEgC", |  | R | 2 | 1 min
|  |  |  | OE012 | Cummulated volume m3 | "338'360'004'Ccl'MtrC'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE012 | Flow l/h | "338'360'004'Ccl'MtrC'Fl", |  | R | 2 | 1 min
|  |  |  | OE012 | Active effect energy cool | "338'360'004'Ccl'MtrC'Pwr", |  | R | 2 | 1 min
|  |  |  | OE012 | Flow temp energy cool | "338'360'004'Ccl'MtrC'TFl", |  | R | 1 | 1 min
|  |  |  | OE012 | Return temp energy cool | "338'360'004'Ccl'MtrC'TRt", |  | R | 1 | 1 min
|  |  |  | OE011 | Cummulated energy heat | "338'360'004'PreHcl'MtrH'CumEg", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'360'004'PreHcl'MtrH'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'360'004'PreHcl'MtrH'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy heat | "338'360'004'PreHcl'MtrH'Pwr", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow temp energy | "338'360'004'PreHcl'MtrH'TFl", |  | R | 1 | 1 min
|  |  |  | OE011 | Return temp energy | "338'360'004'PreHcl'MtrH'TRt", |  | R | 1 | 1 min
|  |  |  | SB531 | Valve cooling coil | "338'360'004'Ccl'Vlv", |  | R/W | 0 | 1 min
|  |  |  | SB521 | Valve Heating coil | "338'360'004'PreHcl'Vlv", |  | R/W | 0 | 1 min
|  |  |  | RT603 | Actual cool setpoint | "338'360'004'PrSp", |  | R/W | 1 | 1 min
|  |  |  | RT603 | Actual heat setpoint | "338'360'004'PrSp1", |  | R/W | 1 | 1 min
|  |  |  | RT403 | Max setpoint heat air supply | "338'360'004'SpSuMaxH", |  | R/W | 1 | 1 min
|  |  |  | RY401 | Fire detector supply air | "338'360'004'FireDet", |  | R | 0 | 1 min
|  |  |  | LV402 | Maintenance switch | "338'360'004'HclEl'MntnSwi", |  | R | 0 | 1 min
|  |  |  | LV402 | Temperature over alarm | "338'360'004'HclEl'Tovr", |  | R | 0 | 1 min
|  |  |  | LV402 | Command onoff | "338'360'004'HclEl'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | LV402 | Command value | "338'360'004'HclEl'StSwi'Mdlt", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Pump error | "338'360'004'PreHcl'Pu'Er", |  | R | 0 | 1 min
|  |  |  | JP421 | Maintenance switch | "338'360'004'PreHcl'Pu'MntnSwi", |  | R | 0 | 1 min
|  |  |  | JP421 | Pump command | "338'360'004'PreHcl'Pu'Cmd", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Enable kick function mosjonering | "338'360'004'PreHcl'Pu'KickFnct.EnFnct", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Reset kick function mosjonering | "338'360'004'PreHcl'Pu'KickFnct.Reset", |  | R/W | 0 | 1 min
|  |  |  | JP421 | Kick function Operation state mosjonering | "338'360'004'PreHcl'Pu'KickFnct.OpSta", |  | R | 0 | 1 min
|  |  |  | JP421 | Kick function output mosjonering | "338'360'004'PreHcl'Pu'KickFnct.Out", |  | R | 0 | 1 min
|  |  |  | KA502 | Damper extract air | "338'360'004'DmpShofEx'Cmd1", |  | R/W | 0 | 1 min
|  |  |  | KA502 | Command value | "338'360'004'DmpShofEx'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | KA401 | Damper supply air | "338'360'004'DmpShofOa'Cmd1", |  | R/W | 0 | 1 min
|  |  |  | KA401 | Command value | "338'360'004'DmpShofOa'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | LK401 | Command value cool | "338'360'004'Ccl'CmdVal", |  | R/W | 0 | 1 min
|  |  |  | LK401 | ManOpSel cooling coil | "338'360'004'SqCtr'CclManOp", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LV402 | ManOpSel El coil | "338'360'004'SqCtr'EclManOp", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LV401 | ManOpSel Heating coil | "338'360'004'SqCtr'HclManMod", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LV403 | ManOpSel Radiator | "338'360'004'SqCtr'RadManOp", |  | R/W | 0 | 1 min | I sekvens | Ute av sekvens
|  |  |  | LC001 | ManOpSel cool pump | "338'360'004'OpModSwi", |  | R/W | 0 | 1 min
|  |  |  | XS0001 | Plant control | "338'360'004'OpModMan", |  | R/W | 0 | 1 min | Av | Forskningsdrift
|  |  |  | XS0002 | Control heating seq | "338'360'004'OpModMan1", |  | R/W | 0 | 1 min | Alle varmesekvenser | Varmebehov 1 uten elvarme

## =433.000
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
|  | 10.205.34.17 | 2443270 | RE001 | El Power Elevator Cummulated | "338'433'000'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE001 | El Power Elevator | "338'433'000'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE002 | El power Solar panel Cummulated | "338'433'000'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE002 | El power Solar panel | "338'433'000'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE003 | =434.401 - RE003 Cummulated | "338'433'000'MtrEl13'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE003 | =434.401 - RE003 | "338'433'000'MtrEl13'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE004 | =434.201 - RE004 Cummulated | "338'433'000'MtrEl14'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE004 | =434.201 - RE004 | "338'433'000'MtrEl14'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE005 | =434.101 - RE005 Cummulated | "338'433'000'MtrEl15'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE005 | =434.101 - RE005 | "338'433'000'MtrEl15'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | QS001 | Common alarm ground | "338'433'000'Mon'CmnFlt", | Fellesfeil jordfeilvarsling | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Cosinus phi | "338'433'000'Mtr'Cosphi", | Cosinus phi | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Average current | "338'433'000'Mtr'CurrAvg", | Gjennomsnitts Strøm | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Neutral current | "338'433'000'Mtr'CurrNeut", | Utligningsstrøm | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Current phase 1 | "338'433'000'Mtr'CurrPh1", | Strøm fase 1 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Current phase 2 | "338'433'000'Mtr'CurrPh2", | Strøm fase 2 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Current phase 3 | "338'433'000'Mtr'CurrPh3", | Strøm fase 3 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Power bought from grid | "338'433'000'Mtr'Eg", | Energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE006 | Nettanalysator Capacitive energy | "338'433'000'Mtr'EgC", | Energi Kapasitiv | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Inductive energy | "338'433'000'Mtr'EgI", | Energi Induktiv | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Frequence | "338'433'000'Mtr'Fq", | Frekvens | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Active effect | "338'433'000'Mtr'PwrActv", | Aktiv effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE006 | Nettanalysator Capacitive effect | "338'433'000'Mtr'PwrC", | Kapasitiv Effekt | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Power factor | "338'433'000'Mtr'PwrFac", | Effektfaktor | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Inductive effect | "338'433'000'Mtr'PwrI", | Induktiv Effekt | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 1-2 | "338'433'000'Mtr'VoltPh12", | Spenning fase 1-2 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 1-3 | "338'433'000'Mtr'VoltPh13", | Spenning fase 1-3 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 1-N | "338'433'000'Mtr'VoltPh1N", | Spenning fase 1-N | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 2-3 | "338'433'000'Mtr'VoltPh23", | Spenning fase 2-3 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 2-N | "338'433'000'Mtr'VoltPh2N", | Spenning fase 2-N | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 2-N | "338'433'000'Mtr'VoltPh3N", | Spenning fase 3-N | R | 2 | 1 min
|  |  |  | QS002 | Common alarm ground | "338'433'000'Mon02'CmnFlt", | Fellesfeil jordfeilvarsling | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator produced energy | "338'433'000'Mtr'PdEgActv", | Produsert aktiv energi | R | 2 | 1 min

## =433.101
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
|  | 10.205.34.11 | 2443266 | RE001 | El power lighting 1 floor Cumulated | "338'433'101'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE001 | El power lighting 1 floor | "338'433'101'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE002 | El power technical 1 floor Cumulated | "338'433'101'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE002 | El power technical 1 floor | "338'433'101'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE003 | El power Warmwater1 cumulated | "338'433'101'MtrEl13'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE003 | El power Warmwater1 | "338'433'101'MtrEl13'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE004 | El power Warmwater2 cumulated | "338'433'101'MtrEl14'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE004 | El power Warmwater2 | "338'433'101'MtrEl14'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE005 | El power HPU1 cumulated | "338'433'101'MtrEl15'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE005 | El power HPU1 | "338'433'101'MtrEl15'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE006 | El power HPU2 cumulated | "338'433'101'MtrEl16'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE006 | El power HPU2 | "338'433'101'MtrEl16'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE007 | El power CPU cumulated | "338'433'101'MtrEl17'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE007 | El power CPU | "338'433'101'MtrEl17'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE008 | El power Frostguard cumulated | "338'433'101'MtrEl18'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE008 | El power Frostguard | "338'433'101'MtrEl18'Pwr", |  | R | 2 | 1 min | Measure | Active_energy

## =433.201
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
|  | 10.205.34.11 | 2443266 | RE201 | El power lighting 2 floor Cumulated | "338'433'201'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE201 | El power lighting 2 floor | "338'433'201'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE202 | El power technical 2 floor Cumulated | "338'433'201'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE202 | El power technical 2 floor | "338'433'201'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy

## =433.301
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
|  | 10.205.34.17 | 2443270 | RE301 | El power lighting 3 floor Cumulated | "338'433'301'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE301 | El power lighting 3 floor | "338'433'301'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE302 | El power technical 3 floor Cumulated | "338'433'301'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE302 | El power technical 3 floor | "338'433'301'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy

## =433.401
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
|  | 10.205.34.17 | 2443270 | RE401 | El power lighting 4 floor Cumulated | "338'433'401'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE401 | El power lighting 4 floor | "338'433'401'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE402 | El power technical 4 floor Cumulated | "338'433'401'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE402 | El power technical 4 floor | "338'433'401'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy

## =434.101
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=471.001 | =434-OU003 | 10.205.34.11 | 2443266 | RE011 | El power PCM pump Cumulated | "338'434'101'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE011 | El power PCM pump Active | "338'434'101'MtrEl11'PwrActv", | Effekt | R | 2 | 1 min | Measure | Active_energy

## =434.201
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=471.001 | =434-OU003 | 10.205.34.12 | 2443265 | RE014 | Power usage Light | "338'434'201'MtrEl20'Pwr", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE014 | Power cummulated Light | "338'434'201'MtrEl20'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE015 | Power usage outlets | "338'434'201'MtrEl13'Pwr", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE015 | Power cummulated outlets | "338'434'201'MtrEl13'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE011 | Power usage Fan =360.004-JV401 | "338'434'201'MtrEl10'PwrActv", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE011 | Power cummulated Fan =360.004-JV401 | "338'434'201'MtrEl10'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE013 | Power usage Fan =360.004-JV501 | "338'434'201'MtrEl16'Pwr", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE013 | Power cummulated Fan =360.004-JV501 | "338'434'201'MtrEl16'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE012 | Power usage El heater =360.004-LV402 | "338'434'201'MtrEl9'PwrActv", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE012 | Power cummulated El heater =360.004-LV402 | "338'434'201'MtrEl9'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE024 | Power usage Light | "338'434'201'MtrEl8'Pwr", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE024 | Power cummulated Light | "338'434'201'MtrEl8'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE025 | Power usage outlets | "338'434'201'MtrEl14'Pwr", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE025 | Power cummulated outlets | "338'434'201'MtrEl14'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE021 | Power usage Fan =360.003-JV401 | "338'434'201'MtrEl4'PwrActv", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE021 | Power cummulated Fan =360.003-JV401 | "338'434'201'MtrEl4'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE023 | Power usage Fan =360.003-JV501 | "338'434'201'MtrEl6'Pwr", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE023 | Power cummulated Fan =360.003-JV501 | "338'434'201'MtrEl6'CumEg", |  | R | 1 | 1 min | Measure | Cumulated
|  |  |  | RE022 | Power usage El heater =360.003-LV402 | "338'434'201'MtrEl7'PwrActv", |  | R | 1 | 1 min | Measure | Active_energy
|  |  |  | RE022 | Power cummulated El heater =360.003-LV402 | "338'434'201'MtrEl7'CumEg", |  | R | 1 | 1 min | Measure | Cumulated

## =434.401
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=471.001 | =434-OU003 | 10.205.34.17 | 2443270 | RE411 | El power Fans 360_001 Cumulated | "338'434'401'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE411 | El power Fans 360_001 | "338'434'401'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE412 | El power Fans 360_002 Cumulated | "338'434'401'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE412 | El power Fans 360_002 | "338'434'401'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE413 | El power Fans 360_007 Cumulated | "338'434'401'MtrEl13'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE413 | El power Fans 360_007 | "338'434'401'MtrEl13'Pwr", | Effekt | R | 2 | 1 min | Measure | Active_energy

## =569.220
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=569.220 | =434.201-OU004 | 10.205.34.32 | 351011 | RB601 | APP Light set | "RSegm220'LgtDev_Grp01", |  | R | 1 | 1 min | Floor,Room | 2,2.20
+338=569.220 | =434.201-OU003 | 10.205.34.14 | 351009 | SQ401 | Supply air VAV air volume flow | "338'569'Flr02'RSegm220'VavSuDev'VavSuAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ401 | Supply air VAV position | "338'569'Flr02'RSegm220'VavSuDev'VavSuPos", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ401 | Setpoint Supply air VAV air volume flow | "338'569'Flr02'RSegm220'VavSuDev'VavSuSpAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ501 | Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass220'VavExDev(501)'VavExAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ501 | Extract air VAV position | "338'569'Flr02'RSegmBaypass220'VavExDev(501)'VavExPos", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ501 | Setpoint Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass220'VavExDev(501)'VavExSpAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ502 | Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass220'VavExDev(502)'VavExAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ502 | Extract air VAV position | "338'569'Flr02'RSegmBaypass220'VavExDev(502)'VavExPos", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SQ502 | Setpoint Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass220'VavExDev(502)'VavExSpAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RB601 | Brightness | "338'569'Flr02'RSegm220'SenDev_1'Brgt", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RB601 | Presence | "338'569'Flr02'RSegm220'SenDev_1'PscDet", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RB601 | Presence HVAC room | "338'569'Flr02'R220'RHvacCoo'RPscDet", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RB601 | Lux value | "338'569'Flr02'RSegm220'Lgt'BrgtCtl'LgtBrgtEff", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RB601 | Setpoint Lux value | "338'569'Flr02'RSegm220'Lgt'BrgtCtl'LgtSpBrgt", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RB602 | Brightness | "338'569'Flr02'RSegm220'SenDev_2'Brgt", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RB602 | Presence | "338'569'Flr02'RSegm220'SenDev_2'PscDet", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp_1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA002 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp_2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA003 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp_3", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA004 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp_4", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA005 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp_5", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA006 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp_6", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA007 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp_7", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr02'RSegm220'VinduStatus'WndContCol", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RG003 | Magnet manual window | "338'569'Flr02'RSegm220'BlsBtnDev'WndCont(1)", | Magnetkontakt vindu uten motor | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RG002 | Magnet manual window | "338'569'Flr02'RSegm220'BlsBtnDev_1'WndCont(2)", | Magnetkontakt vindu uten motor | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RG001 | Magnet manual window | "338'569'Flr02'RSegm220'BlsBtnDev_2'WndCont(3)", | Magnetkontakt vindu uten motor | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | XS604 | Screen command | "338'569'Flr02'RSegm220'BlsDev'BlsCmd(1)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | XS605 | Screen command | "338'569'Flr02'RSegm220'BlsDev'BlsCmd(2)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | XS606 | Screen command | "338'569'Flr02'RSegm220'BlsDev_1'BlsCmd(3)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | XS607 | Screen command | "338'569'Flr02'RSegm220'BlsDev_1'BlsCmd(4)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT900 | Outside air temperature | "CenFnctWeather'WthStn'Toa", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU003 | Manual operation condition | "338'569'Flr02'R220'ROpModDtr", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU003 | Room op mode status | "338'569'Flr02'R220'RHvacCoo'PltModDtr", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU003 | HVAC presence mode | "338'569'Flr02'R220'RHvacCoo'PscModDtr'HvacPscMod", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU003 | APP Room temp setpoint shift | "338'569'Flr02'R220'RHvacCoo'SpTRDtr'SpTRShft", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU003 | Present operating mode | "338'569'Flr02'R220'ROpModDtr'PrOpMod", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr02'RSegm220'VndMot(1)'Sp", |  | R | 1 | 1 min | Floor,Room | 2,2.20
+338=569.220 | =434.201-OU002 | 10.205.34.12 | 2443265 | RT601 | Room temperature | "338'569'220'TR1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT602 | Room temperature | "338'569'220'TR2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT603 | Room temperature | "338'569'220'TCtl'TR3", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU002 | Act setp heating | "338'569'220'TCtl'PrSp", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU002 | Setpoint comfort | "338'569'220'TCtl'SpCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU002 | Setpoint precomfort | "338'569'220'TCtl'SpPreCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OU002 | Setpoint economy | "338'569'220'TCtl'SpEco", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT604 | Room temperature | "338'569'220'TR4", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RH601 | Relative humidity | "338'569'220'Hu1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RH602 | Relative humidity | "338'569'220'Hu2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RY601 | CO2 concentration | "338'569'220'CO2R1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RY602 | CO2 concentration | "338'569'220'CO2R2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RY60X | Act setpoint ppm | "338'569'220'AqCtl'PrSp", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RY60X | Setpoint comfort ppm | "338'569'220'AqCtl'SpCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RY60X | Setpoint precomfort ppm | "338'569'220'AqCtl'SpPreCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RY60X | Setpoint economy ppm | "338'569'220'AqCtl'SpEco", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RD601 | Differential press cell/entrance | "338'569'220'DP1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RD602 | Differential press cell/outdoor | "338'569'220'DP2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OE017 | Cummulated energy heat | "338'360'003'PreHcl'MtrH'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OE017 | Cummulated volume m3 | "338'360'003'PreHcl'MtrH'CumVlm", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OE017 | Flow l/h | "338'360'003'PreHcl'MtrH'Fl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OE017 | Active effect energy heat | "338'360'003'PreHcl'MtrH'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OE017 | Flow temp energy | "338'360'003'PreHcl'MtrH'TFl", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | OE017 | Return temp energy | "338'360'003'PreHcl'MtrH'TRt", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | SB501 | Radiator valve position | "338'569'220'TCtl'Cmd", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE024 | Power usage Light | "338'434'201'MtrEl8'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE024 | Power cummulated Light | "338'434'201'MtrEl8'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE025 | Power usage outlets | "338'434'201'MtrEl14'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE025 | Power cummulated outlets | "338'434'201'MtrEl14'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE021 | Power usage Fan =360.003-JV401 | "338'434'201'MtrEl4'PwrActv", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE021 | Power cummulated Fan =360.003-JV401 | "338'434'201'MtrEl4'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE023 | Power usage Fan =360.003-JV501 | "338'434'201'MtrEl6'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE023 | Power cummulated Fan =360.003-JV501 | "338'434'201'MtrEl6'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE022 | Power usage El heater =360.003-LV402 | "338'434'201'MtrEl7'PwrActv", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RE022 | Power cummulated El heater =360.003-LV402 | "338'434'201'MtrEl7'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.20

## =569.219
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=569.220 | =434.201-OU003 | 10.205.34.14 | 351009 | SQ401 | Supply air VAV air volume flow | "338'569'Flr02'RSegm221'VavSuDev'VavSuAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SQ401 | Supply air VAV position | "338'569'Flr02'RSegm221'VavSuDev'VavSuPos", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SQ401 | Setpoint Supply air VAV air volume flow | "338'569'Flr02'RSegm221'VavSuDev'VavSuSpAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
+338=569.220 | =434.201-OU004 | 10.205.34.32 | 351011 | RB601 | APP Light set | "RSegm219'LgtDev_Grp00", |  | R | 1 | 1 min | Floor,Room | 2,2.19
+338=569.119 | =434.201-OU002 | 10.205.34.13 | 351008 | SQ501 | Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass219'VavExDev(501)'VavExAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SQ501 | Extract air VAV position | "338'569'Flr02'RSegmBaypass219'VavExDev(501)'VavExPos", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SQ501 | Setpoint Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass219'VavExDev(501)'VavExSpAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SQ502 | Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass219'VavExDev(502)'VavExAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SQ502 | Extract air VAV position | "338'569'Flr02'RSegmBaypass219'VavExDev(502)'VavExPos", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SQ502 | Setpoint Extract air VAV air volume flow | "338'569'Flr02'RSegmBaypass219'VavExDev(502)'VavExSpAirFl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RB601 | Brightness | "338'569'Flr02'RSegm219'SenDev_1'Brgt", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RB601 | Presence | "338'569'Flr02'RSegm219'SenDev_1'PscDet", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RB601 | Presence HVAC room | "338'569'Flr02'R219'RHvacCoo'RPscDet", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RB601 | Lux value | "338'569'Flr02'RSegm219'Lgt'BrgtCtl'LgtBrgtEff", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RB601 | Setpoint Lux value | "338'569'Flr02'RSegm219'Lgt'BrgtCtl'LgtSpBrgt", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RB602 | Brightness | "338'569'Flr02'RSegm219'SenDev_2'Brgt", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RB602 | Presence | "338'569'Flr02'RSegm219'SenDev_2'PscDet", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp_S2_X1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA002 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp_S2_X2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA003 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp_S2_X3", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA004 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp_S2_X4", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA005 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp_S2_X5", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA006 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp_S2_X6", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA007 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp_S2_X7", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr02'RSegm219'VinduStatus'WndContCol", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RG003 | Magnet manual window | "338'569'Flr02'RSegm219'BlsBtnDev_1'WndCont(1)", | Magnetkontakt vindu uten motor | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RG002 | Magnet manual window | "338'569'Flr02'RSegm219'BlsBtnDev'WndCont(1)", | Magnetkontakt vindu uten motor | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RG001 | Magnet manual window | "338'569'Flr02'RSegm219'BlsBtnDev_2'WndCont(1)", | Magnetkontakt vindu uten motor | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | XS604 | Screen command | "338'569'Flr02'RSegm219'BlsDev'BlsCmd(1)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | XS605 | Screen command | "338'569'Flr02'RSegm219'BlsDev'BlsCmd(2)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | XS606 | Screen command | "338'569'Flr02'RSegm219'BlsDev_1'BlsCmd(3)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | XS607 | Screen command | "338'569'Flr02'RSegm219'BlsDev_1'BlsCmd(4)", | Screens | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT900 | Outside air temperature | "338'569'Flr02'R219'RHvacCoo'TOa", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Manual operation condition | "338'569'Flr02'R219'ROpModDtr", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Room op mode status | "338'569'Flr02'R219'RHvacCoo'PltModDtr", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | HVAC presence mode | "338'569'Flr02'R219'RHvacCoo'PscModDtr'HvacPscMod", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | APP Room temp setpoint shift | "338'569'Flr02'R219'RHvacCoo'SpTRDtr'SpTRShft", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Present operating mode | "338'569'Flr02'R219'ROpModDtr'PrOpMod", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr02'RSegm219'VndMot(1)'Sp", |  | R | 1 | 1 min | Floor,Room | 2,2.19
| =434.201-OU002 | 10.205.34.12 | 2443265 | RT601 | Room temperature | "338'569'219'TR1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT602 | Room temperature | "338'569'219'TR2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT603 | Room temperature | "338'569'219'TCtl'TR3", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Act setp heating | "338'569'219'TCtl'PrSp", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Setpoint comfort | "338'569'219'TCtl'SpCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Setpoint precomfort | "338'569'219'TCtl'SpPreCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Setpoint economy | "338'569'219'TCtl'SpEco", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OU002 | Setpoint shift | "338'569'219'TCtl'SpShft", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT604 | Room temperature | "338'569'219'TR4", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RH601 | Relative humidity | "338'569'219'Hu1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RH602 | Relative humidity | "338'569'219'Hu2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RY601 | CO2 concentration | "338'569'219'CO2R1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RY602 | CO2 concentration | "338'569'219'CO2R2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RY60X | Act setpoint ppm | "338'569'219'AqCtl'PrSp", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RY60X | Setpoint comfort ppm | "338'569'219'AqCtl'SpCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RY60X | Setpoint precomfort ppm | "338'569'219'AqCtl'SpPreCmf", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RY60X | Setpoint economy ppm | "338'569'219'AqCtl'SpEco", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RD601 | Differential press cell/entrance | "338'569'219'DP1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RD602 | Differential press cell/outdoor | "338'569'219'DP2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OE017 | Cummulated energy heat | "338'360'004'PreHcl'MtrH'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OE017 | Cummulated volume m3 | "338'360'004'PreHcl'MtrH'CumVlm", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OE017 | Flow l/h | "338'360'004'PreHcl'MtrH'Fl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OE017 | Active effect energy heat | "338'360'004'PreHcl'MtrH'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OE017 | Flow temp energy | "338'360'004'PreHcl'MtrH'TFl", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | OE017 | Return temp energy | "338'360'004'PreHcl'MtrH'TRt", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | SB501 | Radiator valve position | "338'569'219'TCtl'Cmd", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE014 | Power usage Light | "338'434'201'MtrEl20'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE014 | Power cummulated Light | "338'434'201'MtrEl20'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE015 | Power usage outlets | "338'434'201'MtrEl13'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE015 | Power cummulated outlets | "338'434'201'MtrEl13'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE011 | Power usage Fan =360.004-JV401 | "338'434'201'MtrEl10'PwrActv", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE011 | Power cummulated Fan =360.004-JV401 | "338'434'201'MtrEl10'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE013 | Power usage Fan =360.004-JV501 | "338'434'201'MtrEl16'Pwr", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE013 | Power cummulated Fan =360.004-JV501 | "338'434'201'MtrEl16'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE012 | Power usage El heater =360.004-LV402 | "338'434'201'MtrEl9'PwrActv", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RE012 | Power cummulated El heater =360.004-LV402 | "338'434'201'MtrEl9'CumEg", |  | R | 1 | 1 min | Floor,Room | 2,2.19
[8 empty] | R | 1 | 1 min | Floor,Room | 2,2.19

## =370.001
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=320.002 | =434-OU001 | 10.205.34.11 | 2443266 | XS001 | Start/stop 370.001 | "338'370'010'OpModSwi", |  | R/W | 0 | 1 min
|  |  |  | RP501 | Pressure sensor expansion | "338'370'001'DPMon501'PSen", |  | R | 1 | 1 min
|  |  |  | IK001 | Operation mode | "338'370'001'RfMch001'SDOpMod", |  | R/W | 0 | 1 min
|  |  |  | IK001 | Heat pump alarm | "338'370'001'RfMch001'SdAlm", |  | R | 0 | 1 min
|  |  |  | IK001 | No flow alarm | "338'370'001'RfMch001'SdAlmFl", |  | R | 0 | 1 min
|  |  |  | IK001 | Compressor status | "338'370'001'RfMch001'SdOpSta", |  | R | 0 | 1 min
|  |  |  | IK001 | Manual mode Cool pump | "338'370'001'RfMch001'SDOpModMa", |  | R | 0 | 1 min
|  |  |  | IK001 | Preset buffer temp | "338'370'001'RfMch001'Tbt", |  | R | 1 | 1 min
|  |  |  | IK001 | Temp return UHS | "338'370'001'RfMch001'Tr", |  | R | 1 | 1 min
|  |  |  | IK001 | Temp supply UHS | "338'370'001'RfMch001'Tt", |  | R | 1 | 1 min
|  |  |  | IK001 | Heat pump alarm | "338'370'001'RfMch001'Alm", |  | R | 0 | 1 min
|  |  |  | IK001 | No flow alarm | "338'370'001'RfMch001'AlmFl", |  | R | 0 | 1 min
|  |  |  | IK001 | Compressor operation status | "338'370'001'RfMch001'OpSta", |  | R | 0 | 1 min
|  |  |  | IK001 | Defrost active | "338'370'001'RfMch001'OpStaDf", |  | R | 0 | 1 min
|  |  |  | IK001 | Temperatur lower heat source | "338'370'001'RfMch001'TSen", |  | R | 1 | 1 min
|  |  |  | IK001 | Temperatur evaporator | "338'370'001'RfMch001'TSenEv", |  | R | 1 | 1 min
|  |  |  | IK001 | Operation mode | "338'370'001'RfMch001'OpMod", |  | R/W | 0 | 1 min
|  |  |  | IK001 | Setpoint | "338'370'001'RfMch001'Sp", |  | R/W | 1 | 1 min
|  |  |  | IK001 | Flowalarm | "338'370'001'RfMch001'AlmFl", |  | R | 0 | 1 min
|  |  |  | IK001 | Setpoint cooling | "338'370'010'SpC", |  | R/W | 1 | 1 min
|  |  |  | OE011 | Cummulated energy cooling | "338'370'001'MtrEg'CumEgC", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'370'001'MtrEg'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'370'001'MtrEg'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy | "338'370'001'MtrEg'Pwr", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow temp energy | "338'370'001'MtrEg'TFl", |  | R | 1 | 1 min
|  |  |  | OE011 | Return temp energy | "338'370'001'MtrEg'TRt", |  | R | 1 | 1 min
|  |  |  | JP401 | Pump | "338'370'001'Pu401'Cmd", |  | R/W | 0 | 1 min
|  |  |  | JP401 | Pump Error | "338'370'001'Pu401'Er", |  | R | 0 | 1 min
|  |  |  | JP401 | Maintenance switch | "338'370'001'Pu401'MntnSwi", |  | R | 0 | 1 min
|  |  |  | RE007 | Cummulated power | "338'433'101'MtrEl17'CumEg", |  | R | 2 | 1 min
|  |  |  | RE007 | Active power | "338'433'101'MtrEl17'PwrActv", |  | R | 2 | 1 min

## =370.010
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=370.010 | =434-OU004 | 10.205.34.17 | 2443270 | OE011 | Cummulated energy heating | "338'370'010'Mtr11'CumEg", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated energy cooling | "338'370'010'Mtr11'CumEgC", |  | R | 2 | 1 min
|  |  |  | OE011 | Cummulated volume m3 | "338'370'010'Mtr11'CumVlm", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow l/h | "338'370'010'Mtr11'Fl", |  | R | 2 | 1 min
|  |  |  | OE011 | Active effect energy | "338'370'010'Mtr11'Pwr", |  | R | 2 | 1 min
|  |  |  | OE011 | Flow temp energy | "338'370'010'Mtr11'TFl", |  | R | 1 | 1 min
|  |  |  | OE011 | Return temp energy | "338'370'010'Mtr11'TRt", |  | R | 1 | 1 min
+338=370.010 | =434-OU003 | 10.205.34.16 | 2443267 | RT432 | Flow temperature | "338'370'010'MxCrt'TFl", |  | R | 1 | 1 min
|  |  |  | RT531 | Return temperature | "338'370'010'MxCrt'TRt", |  | R | 1 | 1 min
|  |  |  | LC001 | LC001 FanCoil command value | "338'370'010'MxCrt'Fnc", |  | R/W | 0 | 1 min
|  |  |  | LC001 | Reset alarm | "338'370'010'ResetAlm", |  | R/W | 0 | 1 min
|  |  |  | LC001 | Active operation mode | "338'370'010'PrOpMod", |  | R/W | 0 | 1 min
|  |  |  | LC001 | Manual operation mode | "338'370'010'OpModMan", |  | R/W | 0 | 1 min
|  |  |  | LC001 | Common alarm | "338'370'010'CmnAlm", |  | R | 0 | 1 min

## =569.408
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=569.408 | =434-OU003 | 10.205.34.16 | 2443267 | LC001 | LC001 FanCoil command value | "338'370'010'MxCrt'Fnc", |  | R/W | 0 | 1 min
|  |  |  | SB531 | SB531 Valve | "338'370'010'MxCrt'Vlv", |  | R/W | 0 | 1 min
|  |  |  | RT601 | Room temperature | "338'360'007'408'TR", |  | R/W | 1 | 1 min
|  |  |  | RT601 | Actual setpoint room | "338'360'007'PrSp1", |  | R | 1 | 1 min
|  |  |  | RT601 | Setpoint research mode room temp | "338'370'010'SpTR1", |  | R/W | 1 | 1 min
|  |  |  | RT601 | Setpoint emergency cool | "338'370'010'SpCrit", |  | R/W | 1 | 1 min
|  |  |  | RT601 | Setpoint room temperature | "338'360'007'SpR", |  | R/W | 1 | 1 min

## =360.007
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=569.408 | =434-OU003 | 10.205.34.16 | 2443267 | KA401 | Damper supply air command | "338'360'007'DmpShofOa", |  | R/W | 1 | 1 min | Floor,Room | 4,4.08
|  |  |  | KA501 | Damper extract air command | "338'360'007'DmpShofEh", |  | R/W | 1 | 1 min | Floor,Room | 4,4.08
|  |  |  | JV501 | Fan extract command | "338'360'007'FanEx'Mdlt", |  | R/W | 1 | 1 min | Floor,Room | 4,4.08
|  |  |  | JV401 | Fan supply command | "338'360'007'FanSu'Mdlt", |  | R/W | 1 | 1 min | Floor,Room | 4,4.08

## =471.001
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=471.001 | =434-OU003 | 10.205.34.16 | 2443267 | LQ003 | Inv3_Total_power_yields | 338'471'001'CrgElSol3'CumEg3 | Total power yields | R | 1 | 1 min | Area,Inverter,MPPT,Measure | East,LQ003,All,Total
|  |  |  | LQ003 | Inv3_MPPT1_Current | 338'471'001'CrgElSol3'Curr1G | MPPT1 Strøm vest felt G | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | West,LQ003,MPPT1,Inv3_Curr,Solarlab
|  |  |  | LQ003 | Inv3_MPPT2_Current | 338'471'001'CrgElSol3'Curr2G | MPPT2 Strøm vest felt G | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | West,LQ003,MPPT2,Inv3_Curr,Solarlab
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'EgTot3 | Total apparent power | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'Fqg3 | Grid frequency | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'PwrActv3 | Nominal active power | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'PwrActvW3 | Total active power | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'RcpwPh3 | Total reactive power | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'StaUn3 | Device Work State | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'T3 | Internal temperature | R | 1 | 1 min
|  |  |  | LQ003 | Inv3_MPPT1_Voltage | 338'471'001'CrgElSol3'Vtg1G | MPPT1 Spenning vest felt G | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | West,LQ003,MPPT1,Inv3_Volt,Solarlab
|  |  |  | LQ003 | Inv3_MPPT2_Voltage | 338'471'001'CrgElSol3'Vtg2G | MPPT2 Spenning vest felt G | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | West,LQ003,MPPT2,Inv3_Volt,Solarlab
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'Alm | Fault/Alarm code | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'CumDay | Daily power yields | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'CumEg3 | Total power yields | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'CumMon | Monthly power yields | R | 1 | 1 min
|  |  |  | LQ001 | Inv1_MPPT1_Current | 338'471'001'CrgElSol1'Curr1G | MPPT1 Strøm tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT1,Inv1_Curr,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT2_Current | 338'471'001'CrgElSol1'Curr2G | MPPT2 Strøm tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT2,Inv1_Curr,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT3_Current | 338'471'001'CrgElSol1'Curr3G | MPPT3 Strøm tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT3,Inv1_Curr,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT4_Current | 338'471'001'CrgElSol1'Curr4G | MPPT4 Strøm tak felt B | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT4,Inv1_Curr,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT5_Current | 338'471'001'CrgElSol1'Curr5G | MPPT5 Strøm tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT5,Inv1_Curr,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT6_Current | 338'471'001'CrgElSol1'Curr6G | MPPT6 Strøm tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT6,Inv1_Curr,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT7_Current | 338'471'001'CrgElSol1'Curr7G | MPPT7 Strøm tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT7,Inv1_Curr,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT8_Current | 338'471'001'CrgElSol1'Curr8G | MPPT8 Strøm øst fasade felt C | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | East,LQ001,MPPT8,Inv1_Curr,Solarlab
|  |  |  | LQ001 | Inv1_MPPT9_Current | 338'471'001'CrgElSol1'Curr9G | MPPT9 Strøm øst fasade felt C | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | East,LQ001,MPPT9,Inv1_Curr,Solarlab
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'DlyDiEgCm | Daily direct energy consumption | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'DlyEpEg | Daily export energy | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'DlyImEg | Daily import energy | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'EgTot3 | Total apparent power | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'FacPw | Power Factor | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'Fqg3 | Grid frequency | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'PwrActv3 | Nominal active power | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'PwrActvW3 | Total active power | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'RcpwPh3 | Total reactive power | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'StaUn3 | Device Work State | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'T3 | Internal temperature | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'TotDcPwr | Total DC power | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'TotDiEgCm | Total direct energy consumption | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'TotEpEg | Total export energy | R | 1 | 1 min
|  |  |  | LQ001 |  | 338'471'001'CrgElSol1'TotImEg | Total import energy | R | 1 | 1 min
|  |  |  | LQ001 | Inv1_MPPT1_Voltage | 338'471'001'CrgElSol1'Vtg1G | MPPT1 Spenning tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT1,Inv1_Volt,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT2_Voltage | 338'471'001'CrgElSol1'Vtg2G | MPPT2 Spenning tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT2,Inv1_Volt,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT3_Voltage | 338'471'001'CrgElSol1'Vtg3G | MPPT3 Spenning tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT3,Inv1_Volt,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT4_Voltage | 338'471'001'CrgElSol1'Vtg4G | MPPT4 Spenning tak felt B | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT4,Inv1_Volt,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT5_Voltage | 338'471'001'CrgElSol1'Vtg5G | MPPT5 Spenning tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT5,Inv1_Volt,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT6_Voltage | 338'471'001'CrgElSol1'Vtg6G | MPPT6 Spenning tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT6,Inv1_Volt,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT7_Voltage | 338'471'001'CrgElSol1'Vtg7G | MPPT7 Spenning tak felt A | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Roof,LQ001,MPPT7,Inv1_Volt,Sunpower375
|  |  |  | LQ001 | Inv1_MPPT8_Voltage | 338'471'001'CrgElSol1'Vtg8G | MPPT8 Spenning Ã¸st fasade felt C | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | East,LQ001,MPPT8,Inv1_Volt,Solarlab
|  |  |  | LQ001 | Inv1_MPPT9_Voltage | 338'471'001'CrgElSol1'Vtg9G | MPPT9 Spenning Ã¸st fasade felt C | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | East,LQ001,MPPT9,Inv1_Volt,Solarlab
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'Alm | Fault/Alarm code | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'CumDay | Daily power yields | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'CumEg3 | Total power yields | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'CumMon | Monthly power yields | R | 1 | 1 min
|  |  |  | LQ002 | Inv2_MPPT1_Current | 338'471'001'CrgElSol2'Curr1G | MPPT1 Strøm pergola felt F | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Pergola,LQ002,MPPT1,Inv2_Curr,Solitek
|  |  |  | LQ002 | Inv2_MPPT2_Current | 338'471'001'CrgElSol2'Curr2G | MPPT2 Strøm pergola felt F | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Pergola,LQ002,MPPT2,Inv2_Curr,Sunpower375
|  |  |  | LQ002 | Inv2_MPPT3_Current | 338'471'001'CrgElSol2'Curr3G | MPPT3 Strøm nord fasade felt H | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | North,LQ002,MPPT3,Inv2_Curr,Sunpower375
|  |  |  | LQ002 | Inv2_MPPT4_Current | 338'471'001'CrgElSol2'Curr4G | MPPT4 Strøm sør fasade felt D | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | South,LQ002,MPPT4,Inv2_Curr,Solarlab
|  |  |  | LQ002 | Inv2_MPPT5_Current | 338'471'001'CrgElSol2'Curr5G | MPPT5 Strøm sør fasade felt E | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | South,LQ002,MPPT5,Inv2_Curr,Solarlab
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'DlyDiEgCm | Daily direct energy consumption | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'DlyEpEg | Daily export energy | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'DlyImEg | Daily import energy | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'EgTot3 | Total apparent power | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'FacPw | Power Factor | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'Fqg3 | Grid frequency | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'PwrActv3 | Nominal active power | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'PwrActvW3 | Total active power | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'RcpwPh3 | Total reactive power | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'StaUn3 | Device Work State | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'T3 | Internal temperature | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'TotDcPwr | Total DC power | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'TotDiEgCm | Total direct energy consumption | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'TotEpEg | Total export energy | R | 1 | 1 min
|  |  |  | LQ002 |  | 338'471'001'CrgElSol2'TotImEg | Total import energy | R | 1 | 1 min
|  |  |  | LQ002 | Inv2_MPPT1_Voltage | 338'471'001'CrgElSol2'Vtg1G | MPPT1 Spenning pergola felt F | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Pergola,LQ002,MPPT1,Inv2_Volt,Solitek
|  |  |  | LQ002 | Inv2_MPPT2_Voltage | 338'471'001'CrgElSol2'Vtg2G | MPPT2 Spenning pergola felt F | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | Pergola,LQ002,MPPT2,Inv2_Volt,Sunpower375
|  |  |  | LQ002 | Inv2_MPPT3_Voltage | 338'471'001'CrgElSol2'Vtg3G | MPPT3 Spenning nord fasade felt H | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | North,LQ002,MPPT3,Inv2_Volt,Sunpower375
|  |  |  | LQ002 | Inv2_MPPT4_Voltage | 338'471'001'CrgElSol2'Vtg4G | MPPT4 Spenning sÃ¸r fasade felt D | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | South,LQ002,MPPT4,Inv2_Volt,Solarlab
|  |  |  | LQ002 | Inv2_MPPT5_Voltage | 338'471'001'CrgElSol2'Vtg5G | MPPT5 Spenning sÃ¸r fasade felt E | R | 1 | 1 min | Area,Inverter,MPPT,Measure,Type | South,LQ002,MPPT5,Inv2_Volt,Solarlab
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'Alm | Fault/Alarm code | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'CumDay | Daily power yields | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'CumMon | Monthly power yields | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'DlyDiEgCm | Daily direct energy consumption | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'DlyEpEg | Daily export energy | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'DlyImEg | Daily import energy | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'FacPw | Power Factor | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'TotDcPwr | Total DC power | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'TotDiEgCm | Total direct energy consumption | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'TotEpEg | Total export energy | R | 1 | 1 min
|  |  |  | LQ003 |  | 338'471'001'CrgElSol3'TotImEg | Total import energy | R | 1 | 1 min

## =577.001
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=471.001 | =434-OU003 | 10.205.34.16 | 2443267 | REXXX |  | "338'471'001'ValCol'CumEg1", | Kumulert energi LQ001 solscelle | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEg2", | Kumulert energi LQ002 solscelle | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEg3", | Kumulert energi LQ003 solscelle | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgLgt1", | Kumulert energi lys | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgLgt2", | Kumulert energi lys | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgLgt3", | Kumulert energi lys | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgLgt4", | Kumulert energi lys | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgtek1", | Kumulert energi teknisk | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgtek2", | Kumulert energi teknisk | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgtek3", | Kumulert energi teknisk | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEgtek4", | Kumulert energi teknisk | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEg4", | Kumulert energi 434.401 | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEg5", | Kumulert energi 434.201 | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol'CumEg6", | Kumulert energi 434.101 | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption HPU01 | "338'471'001'ValCol'CumEgVp1", | Kumulert energi VP001 | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption HPU02 | "338'471'001'ValCol'CumEgVp2", | Kumulert energi VP002 | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption warm water 1 | "338'471'001'ValCol'CumEgVvb1", | Kumulert energi VVB1 | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption Warm water 2 | "338'471'001'ValCol'CumEgVvb2", | Kumulert energi VVB2 | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv10", | Aktiv effekt teknisk 3.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv11", | Aktiv effekt teknisk 4.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv12", | Aktiv effekt VP001 | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv13", | Aktiv effekt VP002 | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv14", | Aktiv effekt VVB1 | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv15", | Aktiv effekt VVB2 | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv16", | Aktiv effekt 434.101 | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv17", | Aktiv effekt 434.201 | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv18", | Aktiv effekt 434.401 | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv2", | Aktiv effekt LQ002 solscelle | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv3", | Aktiv effekt LQ003 solscelle | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv4", | Aktiv effekt lys 1.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv5", | Aktiv effekt lys 2.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv6", | Aktiv effekt lys 3.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv7", | Aktiv effekt lys 4.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv8", | Aktiv effekt teknisk 1.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv9", | Aktiv effekt teknisk 2.etg | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv19", | Aktiv effekt kjølemaskin | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX |  | "338'471'001'ValCol1'PwrActv20", | Aktiv effekt frostsikring | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX | Power consumption lighting | "338'471'001'ValCol'TotPwrLgt", | Total power light | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power production Solar panels | "338'471'001'ValCol'TotPwrSol", | Total power yield solarplant | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption poweroutlets | "338'471'001'ValCol'TotPwrTek", | Total power teknisk | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption Technical automation | "338'471'001'ValCol'TotPwr434", | Total power 434.xxx | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption HPU | "338'471'001'ValCol'TotPwrVp", | Total power varmepumper | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Power consumption Warm water heating | "338'471'001'ValCol'TotPwrVvb", | Total power varmtvannsberedere | R | 1 | 1 min | Measure | Cumulated
|  |  |  | REXXX | Energy production Solar panels | "338'471'001'ValCol1'PwrActvT1", | Total aktiv effekt solceller | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX | Energy consume Light | "338'471'001'ValCol1'PwrActvT2", | Total aktiv effekt lys | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX | Energy consume tech | "338'471'001'ValCol1'PwrActvT3", | Total aktiv effekt teknisk | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX | Energy consume HPU | "338'471'001'ValCol1'PwrActvT4", | Total aktiv effekt VP | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX | Energy consume Warm water | "338'471'001'ValCol1'PwrActvT5", | Total aktiv effekt VVB | R | 1 | 1 min | Measure | Active_energy
|  |  |  | REXXX | Energy consume automation | "338'471'001'ValCol1'PwrActvT6", | Total aktiv effekt 434.xxx | R | 1 | 1 min | Measure | Active_energy
|  | 10.205.34.11 | 2443266 | RE101 | El power lighting 1 floor Cumulated | "338'433'101'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE101 | El power lighting 1 floor | "338'433'101'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE102 | El power technical 1 floor Cumulated | "338'433'101'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE102 | El power technical 1 floor | "338'433'101'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE201 | El power lighting 2 floor Cumulated | "338'433'201'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE201 | El power lighting 2 floor | "338'433'201'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE202 | El power technical 2 floor Cumulated | "338'433'201'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE202 | El power technical 2 floor | "338'433'201'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE003 | El power Warmwater1 cumulated | "338'433'101'MtrEl13'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE003 | El power Warmwater1 | "338'433'101'MtrEl13'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE004 | El power Warmwater2 cumulated | "338'433'101'MtrEl14'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE004 | El power Warmwater2 | "338'433'101'MtrEl14'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE005 | El power HPU1 cumulated | "338'433'101'MtrEl15'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE005 | El power HPU1 | "338'433'101'MtrEl15'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE006 | El power HPU2 cumulated | "338'433'101'MtrEl16'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE006 | El power HPU2 | "338'433'101'MtrEl16'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE007 | El power CPU cumulated | "338'433'101'MtrEl17'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE007 | El power CPU | "338'433'101'MtrEl17'PwrActv", |  | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE008 | El power Frostguard cumulated | "338'433'101'MtrEl18'CumEg", |  | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE008 | El power Frostguard | "338'433'101'MtrEl18'Pwr", |  | R | 2 | 1 min | Measure | Active_energy
|  | 10.205.34.17 | 2443270 | RE001 | El Power Elevator Cummulated | "338'433'000'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE001 | El Power Elevator | "338'433'000'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE002 | El power Solar panel Cummulated | "338'433'000'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE002 | El power Solar panel | "338'433'000'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE003 | =434.401 - RE003 Cummulated | "338'433'000'MtrEl13'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE003 | =434.401 - RE003 | "338'433'000'MtrEl13'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE004 | =434.201 - RE004 Cummulated | "338'433'000'MtrEl14'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE004 | =434.201 - RE004 | "338'433'000'MtrEl14'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE005 | =434.101 - RE005 Cummulated | "338'433'000'MtrEl15'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE005 | =434.101 - RE005 | "338'433'000'MtrEl15'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | QS001 | Common alarm ground | "338'433'000'Mon'CmnFlt", | Fellesfeil jordfeilvarsling | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Cosinus phi | "338'433'000'Mtr'Cosphi", | Cosinus phi | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Average current | "338'433'000'Mtr'CurrAvg", | Gjennomsnitts Strøm | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Neutral current | "338'433'000'Mtr'CurrNeut", | Utligningsstrøm | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Current phase 1 | "338'433'000'Mtr'CurrPh1", | Strøm fase 1 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Current phase 2 | "338'433'000'Mtr'CurrPh2", | Strøm fase 2 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Current phase 3 | "338'433'000'Mtr'CurrPh3", | Strøm fase 3 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Power bought from grid | "338'433'000'Mtr'Eg", | Energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE006 | Nettanalysator Capacitive energy | "338'433'000'Mtr'EgC", | Energi Kapasitiv | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Inductive energy | "338'433'000'Mtr'EgI", | Energi Induktiv | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Frequence | "338'433'000'Mtr'Fq", | Frekvens | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Active effect | "338'433'000'Mtr'PwrActv", | Aktiv effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE006 | Nettanalysator Capacitive effect | "338'433'000'Mtr'PwrC", | Kapasitiv Effekt | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Power factor | "338'433'000'Mtr'PwrFac", | Effektfaktor | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Inductive effect | "338'433'000'Mtr'PwrI", | Induktiv Effekt | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 1-2 | "338'433'000'Mtr'VoltPh12", | Spenning fase 1-2 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 1-3 | "338'433'000'Mtr'VoltPh13", | Spenning fase 1-3 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 1-N | "338'433'000'Mtr'VoltPh1N", | Spenning fase 1-N | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 2-3 | "338'433'000'Mtr'VoltPh23", | Spenning fase 2-3 | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 2-N | "338'433'000'Mtr'VoltPh2N", | Spenning fase 2-N | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator Voltage phase 2-N | "338'433'000'Mtr'VoltPh3N", | Spenning fase 3-N | R | 2 | 1 min
|  |  |  | QS002 | Common alarm ground | "338'433'000'Mon02'CmnFlt", | Fellesfeil jordfeilvarsling | R | 2 | 1 min
|  |  |  | RE006 | Nettanalysator produced energy | "338'433'000'Mtr'PdEgActv", | Produsert aktiv energi | R | 2 | 1 min
|  |  |  | RE401 | El power lighting 4 floor Cumulated | "338'433'401'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE401 | El power lighting 4 floor | "338'433'401'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE402 | El power technical 4 floor Cumulated | "338'433'401'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE402 | El power technical 4 floor | "338'433'401'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE301 | El power lighting 3 floor Cumulated | "338'433'301'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE301 | El power lighting 3 floor | "338'433'301'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE302 | El power technical 3 floor Cumulated | "338'433'301'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE302 | El power technical 3 floor | "338'433'301'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE411 | El power Fans 360_001 Cumulated | "338'434'401'MtrEl11'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE411 | El power Fans 360_001 | "338'434'401'MtrEl11'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE412 | El power Fans 360_002 Cumulated | "338'434'401'MtrEl12'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE412 | El power Fans 360_002 | "338'434'401'MtrEl12'PwrActv", | Aktiv Effekt | R | 2 | 1 min | Measure | Active_energy
|  |  |  | RE413 | El power Fans 360_007 Cumulated | "338'434'401'MtrEl13'CumEg", | Aktiv energi | R | 2 | 1 min | Measure | Cumulated
|  |  |  | RE413 | El power Fans 360_007 | "338'434'401'MtrEl13'Pwr", | Effekt | R | 2 | 1 min | Measure | Active_energy

## =569.
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
=569.312 | =312-OU001 | 10.205.34.62 | 351204 | RT601 | Room temperature | "338'569'Flr03'RSegm312'SenDev'TR", | '=569.312-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.12
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm312'SenDev'HuRelR", | '=569.312-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm312'SenDev'AQualR", | '=569.312-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm312'SenDev_1'Brgt", | '=569.312-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB602 | Brightness | "338'569'Flr03'RSegm312'SenDev_2'Brgt", | '=569.312-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB603 | Brightness | "338'569'Flr03'RSegm312'SenDev_3'Brgt", | '=569.312-RB603 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB604 | Brightness | "338'569'Flr03'RSegm312'SenDev_4'Brgt", | '=569.312-RB604 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB601 | Presence | "338'569'Flr03'R312'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm312'RadVlvPos", | =569.312-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm312'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm312'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R312'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R312'ROpModDtr'ManOpCnd", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'RSegm312'HVAC'PltOpMod", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R312'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R312'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R312'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm312'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm312'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr03'RSegm312'VndMot(1)'Sp", | Setpoint | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | SQ432 | Supply air VAV air volume flow | "338'569'Flr03'RSegm312'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | SQ432 | Supply air VAV position | "338'569'Flr03'RSegm312'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr03'R312'RHvacCoo'RWndSta", | Magnetkontakt vindu | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RG001 | Magnet windows | "338'569'Flr03'RSegm312'BlsBtnDev'WndCont(1)", |  | R | 2 | 1 min | Floor,Room | 3,3.12
|  |  |  | RG002 | Magnet windows | "338'569'Flr03'RSegm312'BlsBtnDev'WndCont(2)", |  | R | 2 | 1 min | Floor,Room | 3,3.12
=569.312 | =312-OU001 | 10.205.34.103 | 33863 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X1", | Window position | R | 0 | 1 min | Floor,Room | 3,3.12
=569.320 | =320-OU001 | 10.205.34.67 | 351209 | RT601 | Room temperature | "338'569'Flr03'RSegm320'SenDev'TR", | =569.320-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.20
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm320'SenDev'HuRelR", | =569.320-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm320'SenDev'AQualR", | =569.320-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm320'SenDev_1'Brgt", | =569.320-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.20
|  |  |  | RB602 | Brightness | "338'569'Flr03'RSegm320'SenDev_2'Brgt", | =569.320-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.20
|  |  |  | RB601 | Presence | "338'569'Flr03'R320'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm320'RadVlvPos", | =569.320-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm320'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm320'HVAC'Toa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R320'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R320'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'R320'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R320'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'R320'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'R320'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'R320'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'R320'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'R320'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R320'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R320'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm320'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm320'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr03'RSegm320'VndMot(1)'Sp", | Setpoint | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | SQ431 | Supply air VAV air volume flow | "338'569'Flr03'RSegm320'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | SQ431 | Supply air VAV position | "338'569'Flr03'RSegm320'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'R320'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'R320'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R320'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'R320'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'R320'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr03'R320'RHvacCoo'RWndSta", | Magnetkontakt vindu | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RG001 | Magnet windows | "338'569'Flr03'RSegm320'BlsBtnDev'WndCont(1)", | =569.320-RG001 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RG002 | Magnet windows | "338'569'Flr03'RSegm320'BlsBtnDev'WndCont(2)", | =569.320-RG002 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RG003 | Magnet windows | "338'569'Flr03'RSegm320'BlsBtnDev_1'WndCont(3)", | =569.320-RG003 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | RG004 | Magnet windows | "338'569'Flr03'RSegm320'BlsBtnDev_1'WndCont(4)", | =569.320-RG004 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | QX001 | Blinds height | "338'569'Flr03'RSegm320'Shd(1)'CenFcd'BlsHgt(1)", | Blinds height 1 | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | QX002 | Blinds height | "338'569'Flr03'RSegm320'Shd_2(3)'CenFcd'BlsHgt(3)", | Blinds height 3 | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | QX003 | Blinds height | "338'569'Flr03'RSegm320'Shd_1(2)'CenFcd'BlsHgt(2)", | Blinds height 2 | R | 2 | 1 min | Floor,Room | 3,3.20
|  |  |  | QX004 | Blinds height | "338'569'Flr03'RSegm320'Shd_4(6)'CenFcd'BlsHgt(6)", | Blinds height 6 | R | 2 | 1 min | Floor,Room | 3,3.20
=569.320 | =320-OU001 | 10.205.34.104 | 33864 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X5", | Window position | R | 2 | 1 min | Floor,Room | 3,3.20
=569.322 | =322-OU001 | 10.205.34.69 | 351211 | RT601 | Room temperature | "338'569'Flr03'RSegm322'SenDev'TR", | =569.322-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.22
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm322'SenDev'HuRelR", | =569.322-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm322'SenDev'AQualR", | =569.322-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm322'SenDev_1'Brgt", | =569.322-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB602 | Brightness | "338'569'Flr03'RSegm322'SenDev_2'Brgt", | =569.322-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB603 | Brightness | "338'569'Flr03'RSegm322'SenDev_3'Brgt", | =569.322-RB603 Lysstyrke | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB604 | Brightness | "338'569'Flr03'RSegm322'SenDev_4'Brgt", | =569.322-RB604 Lysstyrke | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB605 | Brightness | "338'569'Flr03'RSegm322'SenDev_5'Brgt", | =569.322-RB605 Lysstyrke | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB601 | Presence | "338'569'Flr03'R322'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm322'RadVlvPos", | =569.322-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | SB502 | Radiator valve position | "338'569'Flr03'RSegm322'RadVlvPos_1", | =569.322-SB502 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm322'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm322'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R322'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R322'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'R322'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R322'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'R322'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'R322'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'R322'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'R322'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'R322'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R322'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R322'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm322'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm322'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr03'RSegm322'VndMot(1)'Sp", | Setpoint | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | SQ431 | Supply air VAV air volume flow | "338'569'Flr03'RSegm322'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | SQ431 | Supply air VAV position | "338'569'Flr03'RSegm322'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'R322'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'R322'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R322'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'R322'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'R322'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr03'RSegm322'VinduStatus'WndContCol", | Magnetkontakt vindu | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RG001 | Magnet windows | "338'569'Flr03'RSegm322'BlsBtnDev'WndCont(1)", | =569.322-RG001 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | RG002 | Magnet windows | "338'569'Flr03'RSegm322'BlsBtnDev'WndCont(2)", | =569.322-RG002 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | QX001 | Blinds height | "338'569'Flr03'RSegm322'Shd_1(1)'CenFcd'BlsHgt(1)", | Blinds height 1 | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | QX002 | Blinds height | "338'569'Flr03'RSegm322'Shd_2(2)'CenFcd'BlsHgt(2)", | Blinds height 2 | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | QX003 | Blinds height | "338'569'Flr03'RSegm322'Shd_3(3)'CenFcd'BlsHgt(3)", | Blinds height 3 | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | QX004 | Blinds height | "338'569'Flr03'RSegm322'Shd_4(4)'CenFcd'BlsHgt(4)", | Blinds height 4 | R | 2 | 1 min | Floor,Room | 3,3.22
|  |  |  | QX005 | Blinds height | "338'569'Flr03'RSegm322'Shd_5(5)'CenFcd'BlsHgt(5)", | Blinds height 5 | R | 2 | 1 min | Floor,Room | 3,3.22
=569.322 | =322-OU001 | 10.205.34.104 | 33864 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X3", | Window position | R | 2 | 1 min | Floor,Room | 3,3.22
=569.322 | =322-OU001 | 10.205.34.104 | 33864 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X2", | Window position | R | 2 | 1 min | Floor,Room | 3,3.22
=569.321 | =321-OU001 | 10.205.34.104 | 33864 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X4", | Window position | R | 2 | 1 min | Floor,Room | 3,3.21
=569.318 | =318-OU001 | 10.205.34.66 | 351208 | RT601 | Room temperature | "338'569'Flr03'RSegm318'SenDev'TR", | =569.318-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.18
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm318'SenDev'HuRelR", | =569.318-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm318'SenDev'AQualR", | =569.318-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm318'SenDev_1'Brgt", | =569.318-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.18
|  |  |  | RB601 | Presence | "338'569'Flr03'RVavSone317-318'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm318'HVAC'Rad'RadVlvPosVal", | =569.318-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm318'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm318'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R318'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'RVavSone317-318'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'RVavSone317-318'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R318'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R318'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R318'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm318'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm318'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | SQ433 | Supply air VAV air volume flow | "338'569'Flr03'RSegm318'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | SQ433 | Supply air VAV position | "338'569'Flr03'RSegm318'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.18
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'RVavSone317-318'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.18
=569.317 | =317-OU001 | 10.205.34.65 | 351207 | RT601 | Room temperature | "338'569'Flr03'RSegm317'SenDev'TR", | =569.317-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.17
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm317'SenDev'HuRelR", | =569.317-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm317'SenDev'AQualR", | =569.317-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm317'SenDev_1'Brgt", | =569.317-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.17
|  |  |  | RB601 | Presence | "338'569'Flr03'RVavSone317-318'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm317'HVAC'Rad'RadVlvPosVal", | =569.317-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm317'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm317'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R317'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R317'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'R317'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R317'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'R317'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'R317'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'R317'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'R317'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'R317'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R317'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R317'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm317'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm317'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | SQ433 | Supply air VAV air volume flow | "338'569'Flr03'RSegm317'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | SQ433 | Supply air VAV position | "338'569'Flr03'RSegm317'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'R317'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'R317'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R317'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'R317'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.17
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'R317'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.17
=569.316 | =316-OU001 | 10.205.34.64 | 351206 | RB601 | Brightness | "338'569'Flr03'RSegm316'SenDev'Brgt", | =569.316-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.16
|  |  |  | RB602 | Brightness | "338'569'Flr03'RSegm316'SenDev_1'Brgt", | =569.316-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.16
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm316'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 0 | 1 min | Floor,Room | 3,3.16
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm317'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 0 | 1 min | Floor,Room | 3,3.16
|  |  |  | RB601 | Presence | "338'569'Flr03'RSegm316'Lgt'PscOp'LgtPscDetCol'LgtPscDetRs", | Result of lighting presence detector | R | 0 | 1 min | Floor,Room | 3,3.16
|  |  |  | RB601 | APP Light set | [5 empty] | Floor,Room | 3,3.16
=569.323 | =323-OU001 | 10.205.34.70 | 351212 | RT601 | Room temperature | "338'569'Flr03'RSegm323'SenDev'TR", | =569.323-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.23
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm323'SenDev'HuRelR", | =569.323-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm323'SenDev'AQualR", | =569.323-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm323'SenDev_1'Brgt", | =569.323-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.23
|  |  |  | RB601 | Presence | "338'569'Flr03'R323'RHvacCoo'PscModDtr", |  | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm323'RadVlvPos", | =569.323-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm323'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm323'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R323'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R323'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'R323'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R323'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'R323'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'R323'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'R323'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'R323'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'R323'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R323'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R323'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm323'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm323'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr03'RSegm323'VndMot(1)'Sp", | Setpoint | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | SQ431 | Supply air VAV air volume flow | "338'569'Flr03'RSegm323'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | SQ431 | Supply air VAV position | "338'569'Flr03'RSegm323'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'R323'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'R323'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R323'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'R323'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'R323'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr03'RSegm323'VinduStatus'WndContCol", | Magnetkontakt vindu | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RG001 | Magnet windows | "338'569'Flr03'RSegm323'BlsBtnDev'WndCont(1)", | =569.323-RG001 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RG002 | Magnet windows | "338'569'Flr03'RSegm323'BlsBtnDev'WndCont(2)", | =569.323-RG002 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.23
|  |  |  | RG003 | Magnet windows | "338'569'Flr03'RSegm323'BlsBtnDev_1'WndCont(1)", | =569.323-RG003 Magnetkontakt | R | 0 | 1 min | Floor,Room | 3,3.23
|  |  |  | QX001 | Blinds height | "338'569'Flr03'RSegm323'Shd(1)'CenFcd'BlsHgt(1)", | Blinds height 1 | R | 0 | 1 min | Floor,Room | 3,3.23
=569.323 | =323-OU001 | 10.205.34.104 | 33864 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X1", | Window position | R | 0 | 1 min | Floor,Room | 3,3.23
=569.311 | =311-OU001 | 10.205.34.61 | 351203 | RT601 | Room temperature | "338'569'Flr03'RSegm311'SenDev'TR", | =569.311-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.11
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm311'SenDev'HuRelR", | =569.311-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm311'SenDev'AQualR", | =569.311-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm311'SenDev_1'Brgt", | =569.311-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.11
|  |  |  | RB602 | Brightness | "338'569'Flr03'RSegm311'SenDev_2'Brgt", | =569.311-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.11
|  |  |  | RB603 | Brightness | "338'569'Flr03'RSegm311'SenDev_3'Brgt", | =569.311-RB603 Lysstyrke | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RB601 | Presence | "338'569'Flr03'R311'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm311'HVAC'Rad'RadVlvPosVal", | =569.311-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm311'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm311'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R311'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R311'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'R311'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R311'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'R311'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'R311'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'R311'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'R311'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'R311'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R311'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R311'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm311'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm311'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr03'RSegm311'VndMot(1)'Sp", | Setpoint | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | SQ432 | Supply air VAV air volume flow | "338'569'Flr03'RSegm311'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | SQ432 | Supply air VAV position | "338'569'Flr03'RSegm311'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'R311'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'R311'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R311'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'R311'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'R311'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr03'RSegm311'VinduStatus'WndContCol", | Magnetkontakt vindu | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RG001 | Magnet windows | "338'569'Flr03'RSegm311'BlsBtnDev'WndCont(1)", | =569.311-RG001 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RG002 | Magnet windows | "338'569'Flr03'RSegm311'BlsBtnDev'WndCont(2)", | =569.311-RG002 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.11
|  |  |  | RG003 | Magnet windows | "338'569'Flr03'RSegm311'BlsBtnDev_1'WndCont(3)", | =569.311-RG003 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.11
=569.311 | =311-OU001 | 10.205.34.103 | 33863 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X3", | Window position | R | 2 | 1 min | Floor,Room | 3,3.11
=569.311 | =311-OU001 | 10.205.34.103 | 33863 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X2", | Window position | R | 2 | 1 min | Floor,Room | 3,3.11
=569.307 | =307-OU001 | 10.205.34.58 | 351200 | RT601 | Room temperature | "338'569'Flr03'RSegm307'SenDev'TR", | =569.307-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 3,3.07
|  |  |  | RT601 | Room RH | "338'569'Flr03'RSegm307'SenDev'HuRelR", | =569.307-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr03'RSegm307'SenDev'AQualR", | =569.307-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RB601 | Brightness | "338'569'Flr03'RSegm307'SenDev_1'Brgt", | =569.307-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.07
|  |  |  | RB602 | Brightness | "338'569'Flr03'RSegm307'SenDev_2'Brgt", | =569.307-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 3,3.07
|  |  |  | RB601 | Presence | "338'569'Flr03'R307'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | SB501 | Radiator valve position | "338'569'Flr03'RSegm307'HVAC'Rad'RadVlvPosVal", | =569.307-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Dew point temperature | "338'569'Flr03'RSegm307'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RT900 | Outside air temperature | "338'569'Flr03'RSegm307'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present operating mode | "338'569'Flr03'R307'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R307'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'R307'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr03'R307'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr03'R307'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr03'R307'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr03'R307'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr03'R307'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr03'R307'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr03'R307'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr03'R307'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr03'RSegm307'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm307'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | KA001 | APP Window setpoint | "338'569'Flr03'RSegm307'VndMot(1)'Sp", | Setpoint | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | SQ432 | Supply air VAV air volume flow | "338'569'Flr03'RSegm307'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | SQ432 | Supply air VAV position | "338'569'Flr03'RSegm307'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr03'R307'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr03'R307'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R307'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr03'R307'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr03'R307'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | XS601 | Collected Magnet windows | "338'569'Flr03'RSegm307'VinduStatus'WndContCol", | Magnetkontakt vindu | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RG001 | Magnet windows | "338'569'Flr03'RSegm307'BlsBtnDev'WndCont(1)", | =569.307-RG001 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.07
|  |  |  | RG002 | Magnet windows | "338'569'Flr03'RSegm307'BlsBtnDev'WndCont(2)", | =569.307-RG002 Magnetkontakt | R | 2 | 1 min | Floor,Room | 3,3.07
=569.307 | =307-OU001 | 10.205.34.103 | 33863 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X5", | Window position | R | 2 | 1 min | Floor,Room | 3,3.07
=569.307 | =307-OU001 | 10.205.34.103 | 33863 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X4", | Window position | R | 2 | 1 min | Floor,Room | 3,3.07
=569.217 | =217-OU001 | 10.205.34.57 | 338217 | RT601 | Room temperature | "338'569'Flr02'RSegm217'SenDev'TR", | =569.217-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 2,2.17
|  |  |  | RT601 | Room RH | "338'569'Flr02'RSegm217'SenDev'HuRelR", | =569.217-RT601 Relativ fuktighet for rom | R | 2 | 1 min | Floor,Room | 2,2.17
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr02'RSegm217'SenDev'AQualR", | =569.217-RT601 Rom luftkvalitet | R | 2 | 1 min | Floor,Room | 2,2.17
=569.213 | =213-OU001 | 10.205.34.55 | 338213 | RT601 | Room temperature | "338'569'Flr02'RSegm213'SenDev'TR", | =569.213-RT601 Romtemperatur | R | 1 | 2 min | Floor,Room | 2,2.13
|  |  |  | RT601 | Room RH | "338'569'Flr02'RSegm213'SenDev'HuRelR", | =569.213-RT601 Relativ fuktighet for rom | R | 1 | 2 min | Floor,Room | 2,2.13
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr02'RSegm213'SenDev'AQualR", | =569.213-RT601 Rom luftkvalitet | R | 2 | 2 min | Floor,Room | 2,2.13
=569.213 | =213-OU001 | 10.205.34.100 | 33860 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X2", | Window position | R | 2 | 2 min | Floor,Room | 2,2.13
=569.211 | =211-OU001 | 10.205.34.100 | 33860 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X4", | Window position | R | 2 | 2 min | Floor,Room | 2,2.11
=569.211 | =211-OU001 | 10.205.34.100 | 33860 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X3", | Window position | R | 2 | 2 min | Floor,Room | 2,2.11
=569.207 | =207-OU001 | 10.205.34.100 | 33860 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X6", | Window position | R | 2 | 2 min | Floor,Room | 2,2.07
=569.207 | =207-OU001 | 10.205.34.100 | 33860 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X5", | Window position | R | 2 | 2 min | Floor,Room | 2,2.07
=569.108 | =108-OU001 | 10.205.34.100 | 33860 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X1", | Window position | R | 2 | 2 min | Floor,Room | 1,1.08
=569.219 | =434.201-OU002 | 10.205.34.12 | 2443265 | RT601 | Room temperature | "338'569'219'TR1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT602 | Room temperature | "338'569'219'TR2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT603 | Room temperature | "338'569'219'TCtl'TR3", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT604 | Room temperature | "338'569'219'TR4", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT601 | CO2 concentration | "338'569'219'CO2R1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RY602 | CO2 concentration | "338'569'219'CO2R2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RT601 | Relative humidity | "338'569'219'Hu1", |  | R | 1 | 1 min | Floor,Room | 2,2.19
|  |  |  | RH602 | Relative humidity | "338'569'219'Hu2", |  | R | 1 | 1 min | Floor,Room | 2,2.19
=569.219 | =219-OU001 | 10.205.34.101 | 33861 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X1", | Window position | R | 1 | 1 min | Floor,Room | 2,2.19
=569.219 | =219-OU001 | 10.205.34.101 | 33861 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X2", | Window position | R | 1 | 1 min | Floor,Room | 2,2.19
=569.219 | =219-OU001 | 10.205.34.101 | 33861 | KA003 | Window setpoint status | "Auto_position_motor_line_S2_X3", | Window position | R | 1 | 1 min | Floor,Room | 2,2.19
=569.219 | =219-OU001 | 10.205.34.101 | 33861 | KA004 | Window setpoint status | "Auto_position_motor_line_S2_X4", | Window position | R | 1 | 1 min | Floor,Room | 2,2.19
=569.219 | =219-OU001 | 10.205.34.101 | 33861 | KA005 | Window setpoint status | "Auto_position_motor_line_S2_X5", | Window position | R | 1 | 1 min | Floor,Room | 2,2.19
=569.219 | =219-OU001 | 10.205.34.101 | 33861 | KA006 | Window setpoint status | "Auto_position_motor_line_S2_X6", | Window position | R | 1 | 1 min | Floor,Room | 2,2.19
=569.219 | =219-OU001 | 10.205.34.101 | 33861 | KA007 | Window setpoint status | "Auto_position_motor_line_S2_X7", | Window position | R | 1 | 1 min | Floor,Room | 2,2.19
=569.220 | =434.201-OU002 | 10.205.34.12 | 2443265 | RT601 | Room temperature | "338'569'220'TR1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT602 | Room temperature | "338'569'220'TR2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT603 | Room temperature | "338'569'220'TCtl'TR3", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT604 | Room temperature | "338'569'220'TR4", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT601 | CO2 concentration | "338'569'219'CO2R1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RY602 | CO2 concentration | "338'569'219'CO2R2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RT601 | Relative humidity | "338'569'220'Hu1", |  | R | 1 | 1 min | Floor,Room | 2,2.20
|  |  |  | RH602 | Relative humidity | "338'569'220'Hu2", |  | R | 1 | 1 min | Floor,Room | 2,2.20
=569.220 | =434.201-OU002 | 10.205.34.102 | 33862 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X1", | Window position
|  |  |  | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X2", | Window position
|  |  |  | KA003 | Window setpoint status | "Auto_position_motor_line_S2_X3", | Window position
|  |  |  | KA004 | Window setpoint status | "Auto_position_motor_line_S2_X4", | Window position
|  |  |  | KA005 | Window setpoint status | "Auto_position_motor_line_S2_X5", | Window position
|  |  |  | KA006 | Window setpoint status | "Auto_position_motor_line_S2_X6", | Window position
|  |  |  | KA007 | Window setpoint status | "Auto_position_motor_line_S2_X7", | Window position
=569.121 | =121-OU001 | 10.205.34.49 | 350809 | RT601 | Room temperature | "338'569'Flr01'RSegm121'SenDev'TR", | =569.121-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 1,1.21
|  |  |  | RT602 | Room temperature | "338'569'Flr01'RSegm121'SenDev_1'TR", | =569.121-RT602 Romtemperatur | R | 1 | 1 min | Floor,Room | 1,1.21
|  |  |  | RT601 | Room RH | "338'569'Flr01'RSegm121'SenDev'HuRelR", | =569.121-RT601 Relativ fuktighet for rom | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RT602 | Room RH | "338'569'Flr01'RSegm121'SenDev_1'HuRelR", | =569.121-RT602 Relativ fuktighet for rom | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr01'RSegm121'SenDev'AQualR", | =569.121-RT601 Rom luftkvalitet | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RT602 | Room CO2 conc. | "338'569'Flr01'RSegm121'SenDev_1'AQualR", | =569.121-RT602 Rom luftkvalitet | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB601 | Brightness | "338'569'Flr01'RSegm121'SenDev_2'Brgt", | =569.121-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB602 | Brightness | "338'569'Flr01'RSegm121'SenDev_3'Brgt", | =569.121-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB603 | Brightness | "338'569'Flr01'RSegm121'SenDev_4'Brgt", | =569.121-RB603 Lysstyrke | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB604 | Brightness | "338'569'Flr01'RSegm121'SenDev_5'Brgt", | =569.121-RB604 Lysstyrke | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB601 | Presence | "338'569'Flr01'RSegm121'SenDev_2'PscDet", | =569.121-RB601 Bevegelse | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB602 | Presence | "338'569'Flr01'RSegm121'SenDev_3'PscDet", | =569.121-RB602 Bevegelse | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB603 | Presence | "338'569'Flr01'RSegm121'SenDev_4'PscDet", | =569.121-RB603 Bevegelse | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB604 | Presence | "338'569'Flr01'RSegm121'SenDev_5'PscDet", | =569.121-RB604 Bevegelse | R | 0 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB601 | Presence zone | "338'569'Flr01'R121'RHvacCoo'RPscDet", |  | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | SB501 | Radiator valve position | "338'569'Flr01'RSegm121'HVAC'Rad'RadVlvPosVal", | =569.121-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Dew point temperature | "338'569'Flr01'RSegm121'HVAC'TDwp", | Dew point temperature | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | RT900 | Outside air temperature | "338'569'Flr01'RSegm121'HVAC'TOa", | Outside air temperature | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present operating mode | "338'569'Flr01'R121'ROpModDtr'PrOpMod", |  | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Manual operation condition | "338'569'Flr03'R307'ROpModDtr", | Room operating mode determination | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Room op mode status | "338'569'Flr03'R307'RHvacCoo'PltModDtr", | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | HVAC presence mode | "338'569'Flr01'R121'RHvacCoo'PscModDtr'HvacPscMod", | HVAC presence mode | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present heating setpoint | "338'569'Flr01'R121'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present heating setpoint for comfort | "338'569'Flr01'R121'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present heating setpoint for pre-comfort | "338'569'Flr01'R121'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present heating setpoint for economy | "338'569'Flr01'R121'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present heating setpoint for protection | "338'569'Flr01'R121'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Room temperature setpoint | "338'569'Flr01'R121'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | APP Room temp setpoint shift | "338'569'Flr01'R121'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB601 | Lighting effective brightness | "338'569'Flr01'RSegm121'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB601 | Lighting setpoint for brightness | "338'569'Flr01'RSegm121'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_SQ411 | Supply air VAV air volume flow | "338'569'Flr01'RSegm121'VavSuDev(1)'VavSuAirFl(1)", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_SQ411 | Supply air VAV position | "338'569'Flr01'RSegm121'HVAC'VavSuDev(1)'VavSuPos(1)", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_SQ412 | Supply air VAV air volume flow | "338'569'Flr01'RSegm121'VavSuDev(2)'VavSuAirFl(2)", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_SQ412 | Supply air VAV position | "338'569'Flr01'RSegm121'HVAC'VavSuDev(2)'VavSuPos(2)", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_SQ411 | Supply air VAV air volume flow | "338'569'Flr01'RSegm121'VavSuDev(3)'VavSuAirFl(3)", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_SQ411 | Supply air VAV position | "338'569'Flr01'RSegm121'HVAC'VavSuDev(3)'VavSuPos(3)", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_SQ412 | Supply air VAV air volume flow | "338'569'Flr01'RSegm121'VavSuDev(4)'VavSuAirFl(4)", | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_SQ412 | Supply air VAV position | "338'569'Flr01'RSegm121'HVAC'VavSuDev(4)'VavSuPos(4)", | Supply air VAV position | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_SQ411 | Setpoint air volume flow | "338'569'Flr01'RSegm121'VavSuDev(1)'VavSuSpAirFl(1)", | =360.001-SQ411 Supply air VAV setpoint f.air vol.flow 1 | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_SQ412 | Setpoint air volume flow | "338'569'Flr01'RSegm121'VavSuDev(2)'VavSuSpAirFl(2)", | =360.001-SQ412 Supply air VAV setpoint f.air vol.flow 2 | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_SQ411 | Setpoint air volume flow | "338'569'Flr01'RSegm121'VavSuDev(3)'VavSuSpAirFl(3)", | =360.002-SQ411 Tilluft VAV settpunkt for luft vol.flow 3 | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_SQ412 | Setpoint air volume flow | "338'569'Flr01'RSegm121'VavSuDev(4)'VavSuSpAirFl(4)", | =360.002-SQ412 Tilluft VAV settpunkt for luft vol.flow 4 | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_RP411 | Pressure sensor | "338'569'Flr01'RSegm121'Psen", | =360.001-RP411 Trykkføler | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360001_RP412 | Pressure sensor | "338'569'Flr01'RSegm121'Psen_1", | =360.001-RP412 Trykkføler | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_RP411 | Pressure sensor | "338'569'Flr01'RSegm121'Psen_2", | =360.002-RP411 Trykkføler | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | 360002_RP412 | Pressure sensor | "338'569'Flr01'RSegm121'Psen_3", | =360.002-RP412 Trykkføler | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present cooling setpoint | "338'569'Flr01'R121'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present cooling setpoint for comfort | "338'569'Flr01'R121'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present cooling setpoint for pre-comfort | "338'569'Flr01'R121'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present cooling setpoint for economy | "338'569'Flr01'R121'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 1,1.21
|  |  |  | OU001 | Present cooling setpoint for protection | "338'569'Flr01'R121'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 1,1.21
=569.405 | =405-OU001 | 10.205.34.73 | 338405 | RT601 | Room temperature | "338'569'Flr04'RSegm405'SenDev_3'TR", | =569.405-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 4,4.05
|  |  |  | RT602 | Room temperature | "338'569'Flr04'RSegm405'SenDev_4'TR", | =569.405-RT602 Romtemperatur | R | 1 | 1 min | Floor,Room | 4,4.05
|  |  |  | RT601 | Room RH | "338'569'Flr04'RSegm405'SenDev_3'HuRelR", | =569.405-RT601 Relativ fuktighet for rom | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RT602 | Room RH | "338'569'Flr04'RSegm405'SenDev_4'HuRelR", | =569.405-RT602 Relativ fuktighet for rom | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr04'RSegm405'SenDev_3'AQualR", | =569.405-RT601 Rom luftkvalitet | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RT602 | Room CO2 conc. | "338'569'Flr04'RSegm405'SenDev_4'AQualR", | =569.405-RT602 Rom luftkvalitet | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB601 | Brightness |  | =569.121-RB601 Lysstyrke | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB602 | Brightness |  | =569.121-RB602 Lysstyrke | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB603 | Brightness |  | =569.121-RB603 Lysstyrke | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB604 | Brightness |  | =569.121-RB604 Lysstyrke | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB601 | Presence |  | =569.121-RB601 Bevegelse | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB602 | Presence |  | =569.121-RB602 Bevegelse | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB603 | Presence |  | =569.121-RB603 Bevegelse | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB604 | Presence |  | =569.121-RB604 Bevegelse | R | 0 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB601 | Presence zone |  |  | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | SB501 | Radiator valve position |  | =569.121-SB501 Radiator ventil posisjon | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Dew point temperature |  | Dew point temperature | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | RT900 | Outside air temperature |  | Outside air temperature | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present operating mode |  |  | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Manual operation condition |  | Room operating mode determination | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Room op mode status |  | Plant operating mode determination | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | HVAC presence mode |  | HVAC presence mode | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present heating setpoint |  | Present heating setpoint | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present heating setpoint for comfort |  | Present heating setpoint for comfort | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present heating setpoint for pre-comfort |  | Present heating setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present heating setpoint for economy |  | Present heating setpoint for economy | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present heating setpoint for protection |  | Present heating setpoint for protection | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Room temperature setpoint |  | Room temperature setpoint | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | APP Room temp setpoint shift |  | Room temperature setpoint shift | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB601 | Lighting effective brightness |  | Lighting effective brightness | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB601 | Lighting setpoint for brightness |  | Lighting setpoint for brightness | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | RB601 | APP Light set |  |  | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_SQ411 | Supply air VAV air volume flow |  | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_SQ411 | Supply air VAV position |  | Supply air VAV position | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_SQ412 | Supply air VAV air volume flow |  | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_SQ412 | Supply air VAV position |  | Supply air VAV position | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_SQ411 | Supply air VAV air volume flow |  | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_SQ411 | Supply air VAV position |  | Supply air VAV position | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_SQ412 | Supply air VAV air volume flow |  | Supply air VAV air volume flow | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_SQ412 | Supply air VAV position |  | Supply air VAV position | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_SQ411 | Setpoint air volume flow |  | =360.001-SQ411 Supply air VAV setpoint f.air vol.flow 1 | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_SQ412 | Setpoint air volume flow |  | =360.001-SQ412 Supply air VAV setpoint f.air vol.flow 2 | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_SQ411 | Setpoint air volume flow |  | =360.002-SQ411 Tilluft VAV settpunkt for luft vol.flow 3 | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_SQ412 | Setpoint air volume flow |  | =360.002-SQ412 Tilluft VAV settpunkt for luft vol.flow 4 | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_RP411 | Pressure sensor |  | =360.001-RP411 Trykkføler | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360001_RP412 | Pressure sensor |  | =360.001-RP412 Trykkføler | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_RP411 | Pressure sensor |  | =360.002-RP411 Trykkføler | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | 360002_RP412 | Pressure sensor |  | =360.002-RP412 Trykkføler | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present cooling setpoint |  | Present cooling setpoint | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present cooling setpoint for comfort |  | Present cooling setpoint for comfort | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present cooling setpoint for pre-comfort |  | Present cooling setpoint for pre-comfort | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present cooling setpoint for economy |  | Present cooling setpoint for economy | R | 2 | 1 min | Floor,Room | 4,4.05
|  |  |  | OU001 | Present cooling setpoint for protection |  | Present cooling setpoint for protection | R | 2 | 1 min | Floor,Room | 4,4.05
=569.405 | =405-OU001 | 10.205.34.105 | 33865 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X6", | Window position | R | 0 | 1 min | Floor,Room | 4,4.05
=569.405 | =405-OU001 | 10.205.34.105 | 33865 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X5", | Window position | R | 0 | 1 min | Floor,Room | 4,4.05
=569.405 | =405-OU001 | 10.205.34.105 | 33865 | KA003 | Window setpoint status | "Auto_position_motor_line_S2_X1", | Window position | R | 0 | 1 min | Floor,Room | 4,4.05
=569.402 | =402-OU001 | 10.205.34.71 | 338402 | RT601 | Room temperature | "338'569'Flr04'RSegm402'SenDev_5'TR", | =569.402-RT601 Romtemperatur | R | 1 | 1 min | Floor,Room | 4,4.02
|  |  |  | RT602 | Room temperature | "338'569'Flr04'RSegm402'SenDev_6'TR", | =569.402-RT602 Romtemperatur | R | 1 | 1 min | Floor,Room | 4,4.02
|  |  |  | RT601 | Room RH | "338'569'Flr04'RSegm402'SenDev_5'HuRelR", | =569.402-RT601 Relativ fuktighet for rom | R | 0 | 1 min | Floor,Room | 4,4.02
|  |  |  | RT602 | Room RH | "338'569'Flr04'RSegm402'SenDev_6'HuRelR", | =569.402-RT602 Relativ fuktighet for rom | R | 0 | 1 min | Floor,Room | 4,4.02
|  |  |  | RT601 | Room CO2 conc. | "338'569'Flr04'RSegm402'SenDev_5'AQualR", | =569.402-RT601 Rom luftkvalitet | R | 0 | 1 min | Floor,Room | 4,4.02
|  |  |  | RT602 | Room CO2 conc. | "338'569'Flr04'RSegm402'SenDev_6'AQualR", | =569.402-RT602 Rom luftkvalitet | R | 0 | 1 min | Floor,Room | 4,4.02
=569.402 | =402-OU001 | 10.205.34.105 | 33865 | KA005 | Window setpoint status | "Auto_position_motor_line_S2_X2", | Window position | R | 0 | 1 min | Floor,Room | 4,4.02
=569.402 | =402-OU001 | 10.205.34.105 | 33865 | KA004 | Window setpoint status | "Auto_position_motor_line_S2_X3", | Window position | R | 0 | 1 min | Floor,Room | 4,4.02
=569.402 | =402-OU001 | 10.205.34.105 | 33865 | KA001 | Window setpoint status | "Auto_position_motor_line_S2_X4", | Window position | R | 0 | 1 min | Floor,Room | 4,4.02
=569.402 | =402-OU001 | 10.205.34.105 | 33865 | KA002 | Window setpoint status | "Auto_position_motor_line_S2_X8", | Window position | R | 0 | 1 min | Floor,Room | 4,4.02
=569.402 | =402-OU001 | 10.205.34.105 | 33865 | KA003 | Window setpoint status | "Auto_position_motor_line_S2_X7", | Window position | R | 0 | 1 min | Floor,Room | 4,4.02

## Arbeidsark
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
312 | =312-OU001 | 10.205.34.62 | 351204 | -RB602 | Brightness | "338'569'Flr03'RSegm312'SenDev_2'Brgt", | '=569.312-RB602 Lysstyrke | R | 0 | 2 min
|  |  |  | -RB601 | Brightness | "338'569'Flr03'RSegm312'SenDev_1'Brgt", | '=569.312-RB601 Lysstyrke | R | 0 | 2 min
|  |  |  | -RT601 | Room temperature | "338'569'Flr03'RSegm312'SenDev'TR", | '=569.312-RT601 Romtemperatur | R | 1 | 2 min
|  |  |  | -RT601 | Room RH | "338'569'Flr03'RSegm312'SenDev'HuRelR", | '=569.312-RT601 Relativ fuktighet for rom | R | 2 | 2 min
|  |  |  | -RT601 | Room CO2 conc. | "338'569'Flr03'RSegm312'SenDev'AQualR", | '=569.312-RT601 Rom luftkvalitet | R | 2 | 2 min
|  |  |  | -RB603 | Brightness | "338'569'Flr03'RSegm312'SenDev_3'Brgt", | '=569.312-RB603 Lysstyrke | R | 0 | 2 min
|  |  |  | -RB604 | Brightness | "338'569'Flr03'RSegm312'SenDev_4'Brgt", | '=569.312-RB604 Lysstyrke | R | 0 | 2 min
|  |  |  | -SB501 | Radiator valve position | "338'569'Flr03'RSegm312'RadVlvPos", | =569.312-SB501 Radiator ventil posisjon | R | 2 | 2 min
|  |  |  | -RT601 | Dew point temperature | "338'569'Flr03'RSegm312'HVAC'TDwp", | Dew point temperature | R | 2 | 2 min
|  |  |  | -RT900 | Outside air temperature | "338'569'Flr03'RSegm312'HVAC'TOa", | Outside air temperature | R | 2 | 2 min
|  |  |  | -RT601 | Present heating setpoint | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpH", | Present heating setpoint | R | 2 | 2 min
|  |  |  | -RT601 | Present heating setpoint for comfort | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHCmf", | Present heating setpoint for comfort | R | 2 | 2 min
|  |  |  | -RT601 | Present heating setpoint for pre-comfort | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHPcf", | Present heating setpoint for pre-comfort | R | 2 | 2 min
|  |  |  | -RT601 | Present heating setpoint for economy | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHEco", | Present heating setpoint for economy | R | 2 | 2 min
|  |  |  | -RT601 | Present heating setpoint for protection | "338'569'Flr03'R312'RHvacCoo'TCtlH'PrSpHPrt", | Present heating setpoint for protection | R | 2 | 2 min
|  |  |  | -RT601 | Heating setpoint for comfort | "338'569'Flr03'R312'RHvacCoo'TCtlH'SpHCmf", | Heating setpoint for comfort | R | 2 | 2 min
|  |  |  | -RT601 | Delta heating setpoint for pre-comfort | "338'569'Flr03'R312'RHvacCoo'TCtlH'DSpHPcf", | Delta heating setpoint for pre-comfort | R | 2 | 2 min
|  |  |  | -RT601 | Heating setpoint for economy | "338'569'Flr03'R312'RHvacCoo'TCtlH'SpHEco", | Heating setpoint for economy | R | 2 | 2 min
|  |  |  | -RT601 | Heating setpoint for protection | "338'569'Flr03'R312'RHvacCoo'TCtlH'SpHPrt", | Heating setpoint for protection | R | 2 | 2 min
|  |  |  | -RT601 | Room temperature setpoint | "338'569'Flr03'R312'RHvacCoo'SpTRDtr'SpTR", | Room temperature setpoint | R | 2 | 2 min
|  |  |  | -RT601 | Room temperature setpoint shift | "338'569'Flr03'R312'RHvacCoo'SpTRDtr'SpTRShft", | Room temperature setpoint shift | R | 2 | 2 min
|  |  |  | -RB601 | Lighting effective brightness | "338'569'Flr03'RSegm312'Lgt'BrgtCtl'LgtBrgtEff", | Lighting effective brightness | R | 2 | 2 min
|  |  |  | -RB601 | Lighting setpoint for brightness | "338'569'Flr03'RSegm312'Lgt'BrgtCtl'LgtSpBrgt", | Lighting setpoint for brightness | R | 2 | 2 min
|  |  |  | -KA001 | Window setpoint | "338'569'Flr03'RSegm312'VndMot(1)'Sp", | Setpoint | R | 2 | 2 min
|  |  |  | -SQ432 | Supply air VAV air volume flow | "338'569'Flr03'RSegm312'HVAC'VavSu'VavSuAirFl", | Supply air VAV air volume flow | R | 2 | 2 min
|  |  |  | -SQ432 | Supply air VAV position | "338'569'Flr03'RSegm312'HVAC'VavSu'VavSuPos", | Supply air VAV position | R | 2 | 2 min
|  |  |  | -RT601 | Present cooling setpoint | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpC", | Present cooling setpoint | R | 2 | 2 min
|  |  |  | -RT601 | Present cooling setpoint for comfort | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCCmf", | Present cooling setpoint for comfort | R | 2 | 2 min
|  |  |  | -RT601 | Present cooling setpoint for pre-comfort | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCPcf", | Present cooling setpoint for pre-comfort | R | 2 | 2 min
|  |  |  | -RT601 | Present cooling setpoint for economy | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCEco", | Present cooling setpoint for economy | R | 2 | 2 min
|  |  |  | -RT601 | Present cooling setpoint for protection | "338'569'Flr03'R312'RHvacCoo'TCtlC'PrSpCPrt", | Present cooling setpoint for protection | R | 2 | 2 min
|  |  |  | -RT601 | Cooling setpoint for comfort | "338'569'Flr03'R312'RHvacCoo'TCtlC'SpCCmf", | Cooling setpoint for comfort | R | 2 | 2 min
|  |  |  | -RT601 | Delta cooling setpoint for pre-comfort | "338'569'Flr03'R312'RHvacCoo'TCtlC'DSpCPcf", | Delta cooling setpoint for pre-comfort | R | 2 | 2 min
|  |  |  | -RT601 | Cooling setpoint for economy | "338'569'Flr03'R312'RHvacCoo'TCtlC'SpCEco", | Cooling setpoint for economy | R | 2 | 2 min
|  |  |  | -RT601 | Cooling setpoint for protection | "338'569'Flr03'R312'RHvacCoo'TCtlC'SpCPrt", | Cooling setpoint for protection | R | 2 | 2 min
|  |  |  | -XS601 | -RG001/-RG002 Magnet windows | "338'569'Flr03'R312'VinduStatus'WndContCol", | Magnetkontakt vindu | R | 2 | 2 min
405 | =405-OU001 | 10.205.34.73 | 338405 | -RP441 | Pressure | 338'569'Flr04'RSegm405'PSen(1) | =360.001-RP441 TrykkfÃ¸ler | R | 0 | 2 min
|  |  |  | -SQ441 | Supply air VAV position | 338'569'Flr04'RSegm405'VavSuDev'VavSuPos | =360.001-SQ441Tilluft VAV pos
|  |  |  | -SQ441 | Supply air VAV air volume flow | 338'569'Flr04'RSegm405'VavSuDev'VavSuAirFl | =360.001-SQ441Tilluft VAV luft volumstrÃ¸m
|  |  |  | -RT601 | Room temperature | 338'569'Flr04'RSegm405'SenDev_3'TR | =569.405-RT601 Romtemperatur
|  |  |  | -RT601 | Room RH | 338'569'Flr04'RSegm405'SenDev_3'HuRelR | =569.405-RT601 Relativ fuktighet for rom
|  |  |  | -RT601 | Room CO2 conc. | 338'569'Flr04'RSegm405'SenDev_3'AQualR | =569.405-RT601 Rom luftkvalitet
|  |  |  | -RB605 | Brightness | 338'569'Flr04'RSegm405'AP254/02_1'Brgt | =569.405-RB605 Lysstyrke
|  |  |  | -RB604 | Brightness | 338'569'Flr04'RSegm405'AP254/02'Brgt | =569.405-RB604 Lysstyrke
|  |  |  | -RB603 | Brightness | 338'569'Flr04'RSegm405'SenDev_2'Brgt2 | =569.405-RB603 Lysstyrke
|  |  |  | -RB602 | Brightness | 338'569'Flr04'RSegm405'SenDev_1'Brgt2 | =569.405-RB602 Lysstyrke
|  |  |  | -RB601 | Brightness | 338'569'Flr04'RSegm405'SenDev'Brgt2 | =569.405-RB601 Lysstyrke
|  |  |  | -RT602 | Room temperature | 338'569'Flr04'RSegm405'SenDev_4'TR | =569.405-RT602 Romtemperatur
|  |  |  | -RT602 | Room RH | 338'569'Flr04'RSegm405'SenDev_4'HuRelR | =569.405-RT602 Relativ fuktighet for rom
|  |  |  | -RT602 | Room CO2 conc. | 338'569'Flr04'RSegm405'SenDev_4'AQualR | =569.405-RT602 Rom luftkvalitet
|  |  |  | -SB501 | Radiator valve position | 338'569'Flr04'RSegm405'RadVlvPos | =569.405-SB501 Radiator ventil posisjon
|  |  |  | -SQ441 | Setpoint Supply air VAV air volume flow | 338'569'Flr04'RSegm405'VavSuDev'VavSuSpAirFl | =360.001-SQ441Tilluft VAV settpunkt for luft vol.flow
|  |  |  | -RT900 | Dew point temperature | 338'569'Flr04'RSegm405'HVAC'TDwp | Dew point temperature
|  |  |  | -RT900 | Outside air temperature | 338'569'Flr04'RSegm405'HVAC'TOa | Outside air temperature
|  |  |  | -RT601 | Present heating setpoint | 338'569'Flr04'R405'RHvacCoo'TCtlH'PrSpH | Present heating setpoint
|  |  |  | -RT601 | Present heating setpoint for comfort | 338'569'Flr04'R405'RHvacCoo'TCtlH'PrSpHCmf | Present heating setpoint for comfort
|  |  |  | -RT601 | Present heating setpoint for pre-comfort | 338'569'Flr04'R405'RHvacCoo'TCtlH'PrSpHPcf | Present heating setpoint for pre-comfort
|  |  |  | -RT601 | Present heating setpoint for economy | 338'569'Flr04'R405'RHvacCoo'TCtlH'PrSpHEco | Present heating setpoint for economy
|  |  |  | -RT601 | Present heating setpoint for protection | 338'569'Flr04'R405'RHvacCoo'TCtlH'PrSpHPrt | Present heating setpoint for protection
|  |  |  | -RT601 | Heating setpoint for comfort | 338'569'Flr04'R405'RHvacCoo'TCtlH'SpHCmf | Heating setpoint for comfort
|  |  |  | -RT601 | Delta heating setpoint for pre-comfort | 338'569'Flr04'R405'RHvacCoo'TCtlH'DSpHPcf | Delta heating setpoint for pre-comfort
|  |  |  | -RT601 | Heating setpoint for economy | 338'569'Flr04'R405'RHvacCoo'TCtlH'SpHEco | Heating setpoint for economy
|  |  |  | -RT601 | Heating setpoint for protection | 338'569'Flr04'R405'RHvacCoo'TCtlH'SpHPrt | Heating setpoint for protection
|  |  |  | -RT601 | Present cooling setpoint | 338'569'Flr04'R405'RHvacCoo'TCtlC'PrSpC | Present cooling setpoint
|  |  |  | -RT601 | Present cooling setpoint for comfort | 338'569'Flr04'R405'RHvacCoo'TCtlC'PrSpCCmf | Present cooling setpoint for comfort
|  |  |  | -RT601 | Present cooling setpoint for pre-comfort | 338'569'Flr04'R405'RHvacCoo'TCtlC'PrSpCPcf | Present cooling setpoint for pre-comfort
|  |  |  | -RT601 | Present cooling setpoint for economy | 338'569'Flr04'R405'RHvacCoo'TCtlC'PrSpCEco | Present cooling setpoint for economy
|  |  |  | -RT601 | Present cooling setpoint for protection | 338'569'Flr04'R405'RHvacCoo'TCtlC'PrSpCPrt | Present cooling setpoint for protection
|  |  |  | -KA001 | Window setpoint | 338'569'Flr04'RSegm405'VndMot(1)'Sp | Setpoint
|  |  |  | -RG003 | Magnet contact window | 338'569'Flr04'RSegm405'BlsBtnDev'WndCont(1) | =569.405-RG003 Magnetkontakt
|  |  |  | -RG004 | Magnet contact window | 338'569'Flr04'RSegm405'BlsBtnDev'WndCont(2) | =569.405-RG004 Magnetkontakt
|  |  |  | -RG001 | Magnet contact window | 338'569'Flr04'RSegm405'BlsBtnDev_1'WndCont(3) | =569.405-RG001 Magnetkontakt
|  |  |  | -RG001 | Magnet contact window | 338'569'Flr04'RSegm405'BlsBtnDev_1'WndCont(4) | =569.405-RG002 Magnetkontakt
|  |  |  | -RB601 | Presence Col | 338'569'Flr04'R405'RHvacCoo'RPscDet | Room presence detection
[6 empty] | 338'569'Flr04'RSegm405'AP254/02_1'PrphDev_1 | Field device
[6 empty] | 338'569'Flr04'RSegm405'AP254/02'PrphDev_1 | Field device
[6 empty] | 338'569'Flr04'RSegm405'SenDev_2'Sen | Sensor
[6 empty] | 338'569'Flr04'RSegm405'SenDev_1'Sen | Sensor
[6 empty] | 338'569'Flr04'RSegm405'SenDev'Sen | Sensor
[6 empty] | 338'569'Flr04'RSegm405'Lgt'PscOp'LgtPscMod | Lighting presence mode
[6 empty] | 338'569'Flr04'RSegm405'Lgt'PscOp'LgtOpStrgy | Lighting operating strategy
[6 empty] | 338'569'Flr04'RSegm405'HVAC'PltOpMod | Plant operating mode
[6 empty] | 338'569'Flr04'RSegm405'HVAC'HCDmd | Heating/cooling demand
[6 empty] | 338'569'Flr04'RSegm405'RSegmSta | Room segment state
[6 empty] | 338'569'Flr04'R405'RSta | Room state
[6 empty] | 338'569'Flr04'R405'RHvacCoo'HCStaDtr'HCSta | Heating/cooling state
[6 empty] | 338'569'Flr04'R405'RHvacCoo'PscModDtr'HvacPscMod | HVAC presence mode
[6 empty] | 338'569'Flr04'R405'RHvacCoo'PltModDtr'PltOpMod | Plant operating mode
[6 empty] | 338'569'Flr04'R405'RHvacCoo'PltModDtr'NxROpMod | Next room operating mode
[6 empty] | 338'569'Flr04'R405'RHvacCoo'RAQualInd | Room air quality indication
[6 empty] | 338'569'Flr04'R405'RHvacCoo'GrnLf'RHvacEei | Room energy efficiency indication HVAC
[6 empty] | 338'569'Flr04'R405'ROpModDtr'PrOpMod | Present operating mode
[6 empty] | 338'569'Flr04'R405'ROpModDtr'ROpMod | Room operating mode
[6 empty] | 338'569'Flr04'R405'ROpModDtr'ManOpCnd | Manual operation condition
[6 empty] | 338'569'Flr04'R405'ROpModDtr'CenCndTrg | Central condition trigger
[6 empty] | 338'569'Flr04'R405'ROpModDtr'CmfCndTrg | Comfort condition trigger
[6 empty] | 338'569'Flr04'R405'ROpModDtr'EefCndTrg | Energy efficiency condition trigger
[6 empty] | 338'569'Flr04'R405'RLgtCoo'PscModDtr'LgtPscMod | Lighting presence mode
[6 empty] | 338'569'Flr04'RSegm405'SenDev_4'Sen | Sensor
[6 empty] | 338'569'Flr04'RSegm405'SenDev_4'AQualRIndRu | =569.405-RT602 uftkvalitetsindikasjon for romenhet
[6 empty] | 338'569'Flr04'RSegm405'BlsBtnDev'PshBtn | Pushbutton
[6 empty] | 338'569'Flr04'RSegm405'BlsBtnDev_1'PshBtn | Pushbutton
[6 empty] | 338'569'Flr04'RSegm405'Lgt_1'PscOp'LgtPscMod | Lighting presence mode
[6 empty] | 338'569'Flr04'RSegm405'Lgt_1'PscOp'LgtOpStrgy | Lighting operating strategy
[6 empty] | 338'569'Flr04'RSegm405'SenDev_3 | =569.405-RT601 Sensor enhet
[6 empty] | 338'569'Flr04'RSegm405'AP254/02_1 | =569.405-RB605 DagslysfÃ¸ler
[6 empty] | 338'569'Flr04'RSegm405'AP254/02 | =569.405-RB604 DagslysfÃ¸ler
[6 empty] | 338'569'Flr04'RSegm405'SenDev_2 | =569.405-RB603 Sensor enhet
[6 empty] | 338'569'Flr04'RSegm405'SenDev_1 | =569.405-RB602 Sensor enhet
[6 empty] | 338'569'Flr04'RSegm405'SenDev | =569.405-RB601 Sensor enhet
[6 empty] | 338'569'Flr04'RSegm405'Lgt | Lighting
[6 empty] | 338'569'Flr04'RSegm405'Lgt'PscOp | Presence operation
[6 empty] | 338'569'Flr04'RSegm405'Lgt'PscOp'LgtPscDetCol | Collection of lighting presence detector
[6 empty] | 338'569'Flr04'RSegm405'HVAC | HVAC
[6 empty] | 338'569'Flr04'R405'RHvacCoo | Room HVAC coordination
[6 empty] | 338'569'Flr04'R405'RHvacCoo'VntCtl | Ventilation control
[6 empty] | 338'569'Flr04'R405'RHvacCoo'HCStaDtr | Heating/cooling state determination
[6 empty] | 338'569'Flr04'R405'RHvacCoo'TCtlH | Temperature control for heating
[6 empty] | 338'569'Flr04'R405'RHvacCoo'TCtlC | Temperature control for cooling
[6 empty] | 338'569'Flr04'R405'RHvacCoo'SpTRDtr | Room temperature setpoint determination
[6 empty] | 338'569'Flr04'R405'RHvacCoo'RpdVntOp | Rapid ventilation operation
[6 empty] | 338'569'Flr04'R405'RHvacCoo'PscModDtr | Presence mode determination
[6 empty] | 338'569'Flr04'R405'RHvacCoo'PltModDtr | Plant operating mode determination
[6 empty] | 338'569'Flr04'R405'RHvacCoo'AirFlTck | Air volume flow tracking
[6 empty] | 338'569'Flr04'R405'RHvacCoo'GrnLf | Green leaf
[6 empty] | 338'569'Flr04'R405'ROpModDtr | Room operating mode determination
[6 empty] | 338'569'Flr04'R405'RScn | Room scene
[6 empty] | 338'569'Flr04'R405'RLgtCoo | Room lighting coordination
[6 empty] | 338'569'Flr04'R405'RLgtCoo'PscModDtr | Presence mode determination
[6 empty] | 338'569'Flr04'RSegm405'BlsBtnDev | =569.405-XS602 enhet
[6 empty] | 338'569'Flr04'RSegm405'BlsBtnDev_1 | =569.405-XS601 enhet
[6 empty] | 338'569'Flr04'RSegm405'VinduStatus'WndContCol | Collection of window contact
[6 empty] | 338'569'Flr04'RSegm405'VndMot(1) | Vindumotor
338'569'Flr04'RSegm405'VndMot(1)'CmdCol
338'569'Flr04'RSegm405'VndMot(1)'PscDetCol
[6 empty] | 338'569'Flr04'RSegm405'Lgt_1 | Belysning TV
[6 empty] | 338'569'Flr04'RSegm405'Lgt_1'PscOp | Presence operation
[6 empty] | 338'569'Flr04'RSegm405'Lgt_1'PscOp'LgtPscDetCol | Collection of lighting presence detector
[6 empty] | 338'569'Flr04'RSegm405'Lgt'PscOp'LgtDlyOfPscDet | Lighting switch-off delay presence det.
[6 empty] | 338'569'Flr04'RSegm405'Lgt_1'PscOp'LgtDlyOfPscDet | Lighting switch-off delay presence det.

## Kraftflyt
Systemnr | Undersentral | Ipadresse | DeviceID | Component | Name | deviceName | description | Lese/skrive | Desimaler | Polletid | Tag keys | Tag values
+338=433.000 | =434-OU003 | 10.205.34.16 | 2443267 | Vekselretter LQ001 | Akkumulert energi | "338'471'001'ValCol'CumEg1", |  | R | 2 | 1 min
[5 empty] | Aktiv energi | "338'471'001'ValCol1'PwrActv1", |  | R | 2 | 1 min
|  |  |  | Vekselretter LQ001 | Akkumulert energi | "338'471'001'ValCol'CumEg2", |  | R | 2 | 1 min
[5 empty] | Aktiv energi | "338'471'001'ValCol1'PwrActv2", |  | R | 2 | 1 min
|  |  |  | Vekselretter LQ001 | Akkumulert energi | "338'471'001'ValCol'CumEg3", |  | R | 2 | 1 min
[5 empty] | Aktiv energi | "338'471'001'ValCol1'PwrActv3", |  | R | 2 | 1 min
|  |  |  | Solcelleanlegg | Produsert energi | "338'471'001'ValCol'TotPwrSol", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'471'001'ValCol1'PwrActvT1", |  | R | 2 | 1 min
[5 empty] | Inn til bygget forbrukt energi | "338'433'000'MtrEl11'CumEg", |  | R | 2 | 1 min
[5 empty] | Inn til bygget aktiv effekt | "338'433'000'MtrEl11'PwrActv", |  | R | 2 | 1 min
[5 empty] | Ut av bygget avgitt energi | "338'433'000'Mtr'PdEgActv", |  | R | 2 | 1 min
[5 empty] | Ut av bygget aktiv effekt | "338'433'000'Mtr'PwrActv", |  | R | 2 | 1 min
|  |  |  | Belysning | Brukt energi | "338'471'001'ValCol'TotPwrLgt", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'471'001'ValCol1'PwrActvT2", |  | R | 2 | 1 min
|  |  |  | Teknisk | Brukt energi | "338'471'001'ValCol'TotPwrTek", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'471'001'ValCol1'PwrActvT3", |  | R | 2 | 1 min
|  |  |  | Automatikk | Brukt energi | "338'471'001'ValCol'TotPwr434", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'471'001'ValCol1'PwrActvT6", |  | R | 2 | 1 min
|  |  |  | Varmepumper | Brukt energi | "338'471'001'ValCol'TotPwrVp", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'471'001'ValCol1'PwrActvT4", |  | R | 2 | 1 min
|  |  |  | Varmtvannsbereder | Brukt energi | "338'471'001'ValCol'TotPwrVvb", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'471'001'ValCol1'PwrActvT5", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'471'001'ValCol1'PwrActv19", |  | R | 2 | 1 min
|  |  |  | Heis | Produsert energi | "338'433'000'MtrEl15'CumEg", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'433'000'MtrEl15'PwrActv", |  | R | 2 | 1 min
|  |  |  | Nettanalysator | Tilført effekt | "338'433'000'Mtr'Eg", |  | R | 2 | 1 min
+338=433.000 | =434-OU001 | 10.205.34.11 | 2443266 | Frostsikring | Produsert energi | "338'433'101'MtrEl18'CumEg", |  | R | 2 | 1 min
[5 empty] | Aktiv effekt | "338'433'101'MtrEl18'Pwr", |  | R | 2 | 1 min
|  |  |  | Kjølemaskin | Produsert energi | "338'433'101'MtrEl17'CumEg", |  | R | 2 | 1 min